## 153_22
S&C Power Fuses - Type SMU-20 (14.4 kV) | [9 empty] | S&C Power Fuses - Type SMU-20 (14.4 kV) | [9 empty] | S&C Power Fuses - Type SMU-20 (14.4 kV) | [9 empty] | S&C Power Fuses - Type SMU-20 (14.4 kV)
Standard Speed (TCC 153-2-2) | [9 empty] | Standard Speed (TCC 153-2-2) | [9 empty] | Standard Speed (TCC 153-2-2) | [9 empty] | Standard Speed (TCC 153-2-2)
Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
5E |  | 7E |  | 10E |  | 13E |  | 15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
17853 | 0.016504 | 17942.5 | 0.016405 | 18068.5 | 0.016603 | 17978.4 | 0.016504 | 18032.4 | 0.016504 | 17888.7 | 0.016504 | 17835.1 | 0.016504 | 17960.4 | 0.016405 | 17870.8 | 0.016405 | 18268.3 | 0.016405 | 17817.3 | 0.016504 | 18213.6 | 0.016405 | 18177.2 | 0.016405 | 17996.4 | 0.016405 | 17924.5 | 0.016405 | 18068.5 | 0.016504 | 17906.6 | 0.016603
14690 | 0.017092 | 12184.5 | 0.017594 | 14719.4 | 0.017194 | 12834.9 | 0.017507 | 12518 | 0.017507 | 9613.54 | 0.018294 | 12455.6 | 0.017594 | 11706.8 | 0.017896 | 12860.6 | 0.017507 | 13931.7 | 0.017507 | 14485.8 | 0.017507 | 15016.8 | 0.017507 | 14748.9 | 0.017507 | 13642.2 | 0.018094 | 14057.7 | 0.018404 | 15850 | 0.017507 | 16646 | 0.017402
11544 | 0.0177 | 8612.14 | 0.018701 | 11326.8 | 0.017807 | 8450.05 | 0.018701 | 8340.91 | 0.018701 | 6535 | 0.019309 | 8777.33 | 0.018608 | 8021.88 | 0.019098 | 8509.41 | 0.018795 | 10561 | 0.018795 | 11214.1 | 0.018908 | 12135.9 | 0.018608 | 12087.5 | 0.018795 | 11706.8 | 0.019601 | 12555.6 | 0.019897 | 14255.9 | 0.018795 | 15474.1 | 0.018203
9661.73 | 0.018094 | 5848.43 | 0.019699 | 9451.49 | 0.018294 | 5647.27 | 0.019798 | 5398.78 | 0.019997 | 4096.66 | 0.020897 | 6386.41 | 0.019503 | 5819.26 | 0.020503 | 5630.36 | 0.020897 | 8733.56 | 0.019503 | 9575.16 | 0.019601 | 9556.03 | 0.020299 | 10518.8 | 0.020097 | 10860.9 | 0.020606 | 10795.9 | 0.0221 | 13133.5 | 0.019897 | 14485.8 | 0.019098
8257.92 | 0.018497 | 3647.98 | 0.021107 | 7412.54 | 0.019003 | 4023.58 | 0.020897 | 3377.63 | 0.02149 | 2718.75 | 0.023002 | 4721.72 | 0.020897 | 4208.78 | 0.022389 | 4080.31 | 0.023094 | 7479.55 | 0.020401 | 8603.53 | 0.020401 | 8175.75 | 0.021706 | 9623.16 | 0.021191 | 9613.54 | 0.022389 | 9797.94 | 0.023893 | 12307 | 0.021001 | 13225.8 | 0.020606
6754.26 | 0.019098 | 2296.01 | 0.022502 | 5860.14 | 0.019699 | 2936.37 | 0.021902 | 2344.74 | 0.022796 | 2186.22 | 0.024206 | 3684.64 | 0.022389 | 3684.64 | 0.023303 | 3572.17 | 0.024498 | 6160.59 | 0.02149 | 7600.19 | 0.021297 | 6904.5 | 0.023397 | 8586.34 | 0.022502 | 8357.61 | 0.024893 | 9008.54 | 0.025909 | 11406.3 | 0.0223 | 11931.3 | 0.022502
5469.42 | 0.019798 | 1440.76 | 0.024303 | 4637.49 | 0.020503 | 2190.59 | 0.022705 | 1966.34 | 0.023893 | 1935.13 | 0.024893 | 3294.23 | 0.023002 | 3357.42 | 0.023989 | 3114.82 | 0.025909 | 5125.22 | 0.02291 | 6620.51 | 0.0223 | 6099.29 | 0.024893 | 7661.23 | 0.024109 | 7562.28 | 0.026912 | 8054.03 | 0.028605 | 10539.9 | 0.023893 | 10806.7 | 0.024695
4051.85 | 0.020792 | 1124.31 | 0.025909 | 3529.56 | 0.021404 | 1682.32 | 0.023893 | 1798.89 | 0.024695 | 1761.51 | 0.025702 | 2983.73 | 0.023703 | 2995.69 | 0.024794 | 2664.92 | 0.027788 | 4298.1 | 0.024303 | 5825.08 | 0.02349 | 5345.06 | 0.026912 | 6747.51 | 0.026091 | 6767.78 | 0.029594 | 7086.37 | 0.032904 | 9546.48 | 0.026195 | 9661.73 | 0.027788
3121.06 | 0.021706 | 981.352 | 0.026993 | 2729.65 | 0.022211 | 1429.28 | 0.025093 | 1523.75 | 0.026195 | 1603.47 | 0.026698 | 2726.92 | 0.024303 | 2735.11 | 0.025702 | 2323.73 | 0.030012 | 3721.67 | 0.025805 | 4909.5 | 0.025396 | 4812.29 | 0.028893 | 6111.5 | 0.027788 | 5996.48 | 0.032805 | 6216.29 | 0.037697 | 8655.31 | 0.029008 | 8768.56 | 0.030895
2435.55 | 0.022389 | 888.852 | 0.027788 | 2255.05 | 0.022705 | 1162.03 | 0.026912 | 1310.19 | 0.027401 | 1453.79 | 0.028011 | 2450.21 | 0.024993 | 2484.75 | 0.026591 | 2038.42 | 0.032414 | 3209.69 | 0.027511 | 4302.4 | 0.027292 | 4319.64 | 0.031393 | 5513.35 | 0.029802 | 5323.72 | 0.03651 | 5568.76 | 0.042888 | 7630.65 | 0.033201 | 7676.57 | 0.036183
1849.98 | 0.02321 | 822.157 | 0.028491 | 1798.89 | 0.023303 | 986.271 | 0.028491 | 1129.95 | 0.028893 | 1308.88 | 0.029506 | 2212.61 | 0.025909 | 2314.45 | 0.027292 | 1813.34 | 0.035008 | 2901.34 | 0.029212 | 3804.46 | 0.029594 | 3854.24 | 0.034695 | 5028.76 | 0.032188 | 4919.33 | 0.039393 | 4889.91 | 0.05038 | 6890.7 | 0.037285 | 6815.32 | 0.041704
1667.24 | 0.02349 | 735.044 | 0.029802 | 1483.16 | 0.024109 | 844.657 | 0.030895 | 959.038 | 0.031487 | 1199.82 | 0.030895 | 2000.05 | 0.026805 | 2125.85 | 0.028491 | 1639.14 | 0.037811 | 2599.12 | 0.031393 | 3421.82 | 0.032285 | 3387.77 | 0.039314 | 4550.21 | 0.034904 | 4532.04 | 0.043406 | 4221.43 | 0.060678 | 6210.07 | 0.042292 | 6002.48 | 0.049382
1517.66 | 0.023893 | 622.617 | 0.031709 | 1266.39 | 0.025396 | 741.69 | 0.033501 | 828.76 | 0.034384 | 1096.55 | 0.033003 | 1759.75 | 0.028207 | 1972.25 | 0.029594 | 1472.81 | 0.041704 | 2319.09 | 0.034315 | 3028.82 | 0.035502 | 2986.71 | 0.045087 | 4196.17 | 0.037697 | 4175.24 | 0.047588 | 3703.11 | 0.072573 | 5624.73 | 0.047684 | 5286.59 | 0.058826
1385.65 | 0.024206 | 553.317 | 0.033501 | 1092.18 | 0.026591 | 673.125 | 0.035895 | 727.731 | 0.037811 | 993.199 | 0.035787 | 1578.02 | 0.029892 | 1827.91 | 0.030895 | 1328.66 | 0.04609 | 2034.34 | 0.038191 | 2635.76 | 0.04039 | 2612.15 | 0.05291 | 3842.69 | 0.041206 | 3766.6 | 0.053979 | 3241.94 | 0.086712 | 5074.22 | 0.054904 | 4513.95 | 0.073522
1236.36 | 0.024794 | 480.07 | 0.036002 | 959.038 | 0.028095 | 594.031 | 0.039789 | 644.794 | 0.042081 | 903.188 | 0.038807 | 1427.85 | 0.031804 | 1678.96 | 0.032609 | 1187.88 | 0.052174 | 1804.3 | 0.042888 | 2370.67 | 0.045494 | 2349.43 | 0.059775 | 3483.97 | 0.045998 | 3452.76 | 0.060315 | 2898.44 | 0.10288 | 4518.47 | 0.064173 | 4007.52 | 0.088022
1122.07 | 0.025295 | 415.686 | 0.039393 | 875.619 | 0.029212 | 513.85 | 0.045403 | 561.679 | 0.048019 | 814.79 | 0.042888 | 1290.68 | 0.03411 | 1525.27 | 0.034695 | 1053.56 | 0.060015 | 1627.71 | 0.048211 | 2113.14 | 0.052018 | 2106.81 | 0.069102 | 3155.58 | 0.051707 | 3105.49 | 0.071278 | 2562.99 | 0.12529 | 4092.57 | 0.073965 | 3561.47 | 0.10591
1018.34 | 0.025805 | 367.576 | 0.043103 | 803.463 | 0.030313 | 440.509 | 0.053817 | 491.731 | 0.056013 | 718.331 | 0.049185 | 1141.3 | 0.037697 | 1405.19 | 0.036803 | 929.764 | 0.070428 | 1439.32 | 0.055511 | 1822.43 | 0.062277 | 1876.06 | 0.080769 | 2858.15 | 0.058826 | 2735.11 | 0.086799 | 2273.16 | 0.15196 | 3666.26 | 0.086799 | 3133.57 | 0.12846
930.694 | 0.0263 | 311.978 | 0.049382 | 736.516 | 0.031487 | 376.505 | 0.065208 | 426.21 | 0.066726 | 633.925 | 0.056917 | 1021.4 | 0.041913 | 1281.68 | 0.039511 | 813.162 | 0.084486 | 1286.82 | 0.064173 | 1601.87 | 0.073596 | 1726.63 | 0.091158 | 2573.26 | 0.067734 | 2413.73 | 0.10444 | 2024.2 | 0.18394 | 3307.43 | 0.10166 | 2743.33 | 0.15943
859.139 | 0.026912 | 281.162 | 0.055014 | 684.666 | 0.032805 | 315.744 | 0.082236 | 357.427 | 0.084318 | 516.942 | 0.074634 | 910.443 | 0.047209 | 1186.69 | 0.042081 | 685.351 | 0.10848 | 1160.87 | 0.073375 | 1410.82 | 0.088022 | 1532.92 | 0.10827 | 2302.91 | 0.078775 | 2138.65 | 0.12642 | 1791.71 | 0.22556 | 2992.69 | 0.12001 | 2425.83 | 0.19649
789.13 | 0.027511 | 252.127 | 0.061472 | 624.487 | 0.034695 | 260.065 | 0.10892 | 308.256 | 0.10412 | 429.203 | 0.096698 | 820.514 | 0.053495 | 1073.77 | 0.045998 | 585.772 | 0.14168 | 1013.26 | 0.088996 | 1222.83 | 0.10827 | 1331.32 | 0.13303 | 2081.67 | 0.092074 | 1887.35 | 0.15549 | 1598.67 | 0.27966 | 2664.92 | 0.14571 | 2147.22 | 0.24484
721.932 | 0.028207 | 219.847 | 0.072937 | 574.173 | 0.036693 | 223.84 | 0.13888 | 268.79 | 0.13014 | 366.475 | 0.12579 | 737.253 | 0.061288 | 954.255 | 0.052383 | 487.325 | 0.19767 | 913.178 | 0.10412 | 1083.47 | 0.12923 | 1158.55 | 0.16643 | 1857.39 | 0.10903 | 1637.5 | 0.19806 | 1436.45 | 0.34364 | 2330.71 | 0.18284 | 1864.83 | 0.31945
669.098 | 0.028893 | 190.363 | 0.087234 | 525.805 | 0.038884 | 183.815 | 0.19163 | 234.377 | 0.16216 | 318.28 | 0.15879 | 666.427 | 0.070923 | 848.043 | 0.060015 | 407.455 | 0.27413 | 815.606 | 0.12429 | 920.513 | 0.1671 | 1044.12 | 0.20146 | 1655.61 | 0.13171 | 1429.28 | 0.25356 | 1286.82 | 0.42225 | 2069.22 | 0.22646 | 1680.64 | 0.39845
613.961 | 0.029713 | 158.845 | 0.11235 | 483.926 | 0.041787 | 144.884 | 0.27994 | 199.125 | 0.2137 | 275.044 | 0.20348 | 588.708 | 0.085165 | 749.144 | 0.070498 | 339.995 | 0.38168 | 729.917 | 0.1494 | 802.66 | 0.21031 | 942.872 | 0.23951 | 1477.24 | 0.15895 | 1231.42 | 0.33049 | 1148.17 | 0.53357 | 1864.83 | 0.27661 | 1532.92 | 0.48667
569.029 | 0.030496 | 135.359 | 0.14368 | 433.084 | 0.046321 | 120.534 | 0.37902 | 172.765 | 0.27358 | 239.59 | 0.25739 | 517.459 | 0.10475 | 659.137 | 0.083813 | 288.568 | 0.52668 | 647.378 | 0.18211 | 676.499 | 0.28703 | 848.043 | 0.28732 | 1348.74 | 0.18579 | 1074.84 | 0.42352 | 1033.73 | 0.66222 | 1653.96 | 0.35304 | 1395.39 | 0.61253
521.616 | 0.031487 | 112.948 | 0.19106 | 372.759 | 0.053817 | 100.88 | 0.51884 | 142.157 | 0.3813 | 203.554 | 0.34467 | 457.113 | 0.12962 | 554.979 | 0.10837 | 246.887 | 0.71451 | 581.105 | 0.22154 | 574.173 | 0.38823 | 759.706 | 0.34779 | 1196.23 | 0.22874 | 958.08 | 0.53091 | 957.122 | 0.77868 | 1489.1 | 0.43294 | 1271.47 | 0.76939
484.894 | 0.032414 | 97.3131 | 0.2441 | 339.655 | 0.059715 | 84.939 | 0.71953 | 121.259 | 0.49502 | 173.631 | 0.45787 | 397.395 | 0.16395 | 488.301 | 0.13343 | 215.063 | 0.94823 | 513.336 | 0.27799 | 484.894 | 0.53786 | 642.863 | 0.47324 | 1076.99 | 0.27799 | 854 | 0.66954 | 898.683 | 0.89748 | 1265.13 | 0.6156 | 1160.87 | 0.97029
447.167 | 0.033703 | 83.842 | 0.31032 | 297.356 | 0.069379 | 73.5477 | 0.95489 | 103.641 | 0.65432 | 150.194 | 0.59264 | 337.961 | 0.21521 | 407.455 | 0.18174 | 187.341 | 1.2851 | 465.416 | 0.33248 | 422.391 | 0.72169 | 559.437 | 0.6156 | 963.845 | 0.34467 | 791.501 | 0.78887 | 851.442 | 1.0427 | 1162.03 | 0.76097 | 1059.9 | 1.236
410.728 | 0.035008 | 70.0307 | 0.42056 | 262.679 | 0.081092 | 62.7359 | 1.3137 | 89.2047 | 0.87096 | 122.478 | 0.87533 | 273.672 | 0.30877 | 345.824 | 0.24168 | 165.163 | 1.7451 | 427.063 | 0.38939 | 367.209 | 0.97613 | 479.59 | 0.83347 | 867.774 | 0.42352 | 735.044 | 0.92205 | 797.061 | 1.231 | 1053.56 | 0.98299 | 986.271 | 1.5111
375.753 | 0.036693 | 57.9125 | 0.57917 | 227.678 | 0.097377 | 52.6641 | 1.8924 | 80.9583 | 1.0521 | 105.418 | 1.1663 | 228.59 | 0.42183 | 290.886 | 0.33348 | 150.646 | 2.2141 | 380.669 | 0.47895 | 321.8 | 1.3032 | 429.203 | 1.0553 | 768.108 | 0.53464 | 695.013 | 1.068 | 740.208 | 1.4931 | 964.81 | 1.2434 | 934.424 | 1.8164
345.479 | 0.038305 | 48.4695 | 0.79282 | 200.523 | 0.11565 | 48.2277 | 2.2975 | 72.6704 | 1.3322 | 91.2802 | 1.5618 | 194.597 | 0.55981 | 249.368 | 0.44257 | 139.621 | 2.7562 | 347.21 | 0.57112 | 288.28 | 1.6885 | 383.343 | 1.3564 | 678.532 | 0.69617 | 653.885 | 1.2647 | 688.786 | 1.8073 | 888.852 | 1.5759 | 888.852 | 2.1681
317.644 | 0.040189 | 41.1381 | 1.0875 | 173.978 | 0.14282 | 45.0573 | 2.7016 | 66.2168 | 1.6435 | 82.0176 | 1.9775 | 164.668 | 0.76402 | 208.498 | 0.61253 | 131.885 | 3.3229 | 312.29 | 0.69966 | 263.995 | 2.0935 | 348.602 | 1.7226 | 608.46 | 0.87971 | 611.51 | 1.4812 | 648.026 | 2.1702 | 837.089 | 1.9057 | 842.97 | 2.6587
291.468 | 0.042292 | 35.9071 | 1.4504 | 150.345 | 0.17814 | 41.9691 | 3.2571 | 59.6166 | 2.0977 | 74.3612 | 2.4889 | 143.873 | 0.98102 | 180.898 | 0.81452 | 124.702 | 3.9862 | 284.272 | 0.83764 | 247.134 | 2.4715 | 319.875 | 2.1209 | 542.903 | 1.1466 | 572.453 | 1.7857 | 615.805 | 2.5064 | 801.056 | 2.2119 | 809.916 | 3.2022
270.678 | 0.044415 | 31.9105 | 1.9019 | 127.987 | 0.2276 | 39.4855 | 3.807 | 54.2137 | 2.6827 | 68.644 | 3.0828 | 131.49 | 1.1698 | 163.192 | 1.0231 | 119.215 | 4.8445 | 255.681 | 1.0521 | 232.277 | 2.9383 | 297.654 | 2.6402 | 491.731 | 1.4432 | 542.361 | 2.0706 | 585.772 | 2.9266 | 777.381 | 2.5089 | 778.938 | 3.7918
250.368 | 0.047021 | 28.5009 | 2.4914 | 112.723 | 0.2856 | 37.4473 | 4.401 | 50.8527 | 3.2344 | 63.8115 | 3.7729 | 122.355 | 1.3537 | 143.585 | 1.3537 | 115.23 | 5.829 | 234.377 | 1.2723 | 219.408 | 3.4275 | 282.854 | 3.1138 | 450.308 | 1.8019 | 515.909 | 2.425 | 565.06 | 3.3731 | 749.144 | 2.8687 | 752.146 | 4.5533
232.045 | 0.049878 | 26.1522 | 3.0766 | 98.8826 | 0.35874 | 35.5854 | 5.1595 | 47.7001 | 3.919 | 60.6994 | 4.3922 | 111.936 | 1.6468 | 132.281 | 1.6584 | 110.712 | 7.1481 | 214.848 | 1.5509 | 210.173 | 3.8917 | 269.059 | 3.7242 | 425.358 | 2.1061 | 496.176 | 2.7978 | 546.17 | 3.9269 | 726.277 | 3.3262 | 731.378 | 5.4512
216.574 | 0.05291 | 23.9013 | 3.9308 | 85.7927 | 0.45833 | 34.0535 | 6.0427 | 45.2378 | 4.6825 | 57.4511 | 5.2585 | 103.641 | 1.952 | 121.623 | 2.0296 | 107.332 | 8.7657 | 198.727 | 1.8661 | 202.539 | 4.4231 | 261.107 | 4.2539 | 405.018 | 2.4202 | 480.07 | 3.1799 | 530.029 | 4.5669 | 704.812 | 3.7729 | 708.345 | 6.6183
202.944 | 0.056125 | 22.4869 | 4.6825 | 75.7875 | 0.57859 | 32.7183 | 6.9438 | 42.9886 | 5.5614 | 55.1984 | 6.2329 | 94.5316 | 2.3985 | 113.174 | 2.474 | 104.056 | 11.0988 | 182.898 | 2.316 | 195.964 | 5.0473 | 251.875 | 4.9226 | 381.05 | 2.8801 | 464.022 | 3.713 | 515.394 | 5.3007 | 683.982 | 4.4099 | 690.165 | 8.1242
191.508 | 0.05918 | 21.4116 | 5.397 | 67.4195 | 0.71451 | 31.404 | 8.1976 | 41.303 | 6.5394 | 52.7695 | 7.3731 | 88.3171 | 2.8458 | 106.052 | 2.912 | 100.88 | 13.983 | 171.217 | 2.7978 | 189.982 | 5.7999 | 244.43 | 5.7652 | 361.38 | 3.363 | 449.858 | 4.2074 | 505.188 | 6.2329 | 662.441 | 5.098 | 671.109 | 9.9031
180.717 | 0.063092 | 20.4695 | 6.3018 | 59.557 | 0.90923 | 30.2935 | 9.6104 | 39.3672 | 7.9713 | 50.498 | 8.9517 | 83.5073 | 3.303 | 100.779 | 3.4413 | 98.5864 | 17.7227 | 162.216 | 3.2964 | 184.737 | 6.6715 | 238.157 | 6.7049 | 346.863 | 3.919 | 438.312 | 4.9325 | 491.731 | 7.4547 | 648.026 | 5.7883 | 656.505 | 12.1806
169.005 | 0.067531 | 19.6668 | 7.2925 | 52.1922 | 1.1922 | 29.2809 | 11.3798 | 37.7481 | 9.7947 | 48.276 | 11.2779 | 79.2759 | 3.8761 | 95.7685 | 4.0102 | 97.0216 | 21.9298 | 153.689 | 3.88 | 179.995 | 7.6971 | 231.35 | 8.0917 | 333.263 | 4.6966 | 425.358 | 5.7078 | 479.11 | 8.9338 | 632.659 | 6.6915 | 642.22 | 15.3152
159.004 | 0.072283 | 18.8768 | 8.5151 | 46.7089 | 1.5081 | 28.5865 | 13.4213 | 36.6324 | 11.7147 | 46.943 | 13.5562 | 75.0334 | 4.5898 | 90.9158 | 4.8736 | 95.0054 | 28.2148 | 146.193 | 4.5761 | 174.327 | 9.345 | 224.064 | 9.913 | 322.445 | 5.5614 | 415.686 | 6.5328 | 466.814 | 11.0324 | 618.892 | 7.6894 | 623.863 | 19.4889
148.7 | 0.078225 | 18.2275 | 10.2455 | 41.6764 | 1.9306 | 28.1609 | 16.3601 | 35.6566 | 14.3801 | 45.8298 | 16.2948 | 70.3114 | 5.6004 | 87.1764 | 5.668 | 93.591 | 36.8128 | 140.883 | 5.3594 | 169.005 | 11.4483 | 217.224 | 12.2661 | 311.666 | 6.5787 | 405.829 | 7.4696 | 457.113 | 13.4347 | 606.031 | 8.8184 | 608.46 | 25.2505
139.481 | 0.08474 | 17.7065 | 11.9752 | 37.9752 | 2.3557 | 28.1046 | 64.2543 | 34.9855 | 17.3891 | 45.0573 | 19.8429 | 66.6153 | 6.7049 | 83.7582 | 6.5919 | 92.4746 | 49.0504 | 136.174 | 6.3652 | 164.503 | 13.9411 | 211.226 | 15.3152 | 300.045 | 7.8526 | 396.998 | 8.6785 | 447.167 | 16.5741 | 592.251 | 10.442 | 596.412 | 32.5848
132.149 | 0.09007 | 17.2866 | 14.4088 | 35.5143 | 2.7369 | 28.0485 | 167.477 | 34.4646 | 21.3456 | 44.5643 | 24.627 | 63.3664 | 8.1649 | 80.8773 | 7.8369 | 91.0068 | 74.2063 | 132.414 | 7.6358 | 159.482 | 18.1531 | 206.217 | 19.7044 | 289.725 | 9.5529 | 387.971 | 10.5154 | 437.436 | 20.8602 | 580.524 | 12.0835 | 583.434 | 43.1571
123.338 | 0.098651 | 17.0122 | 17.599 | 33.5801 | 3.0952 | 28.0204 | 276.954 | 33.8837 | 27.0002 | 44.0328 | 31.4012 | 60.2158 | 10.1233 | 78.9594 | 8.9249 | 89.4727 | 113.618 | 128.757 | 9.1234 | 155.389 | 23.1003 | 200.925 | 24.9243 | 281.162 | 11.7616 | 378.392 | 12.6144 | 431.355 | 26.3863 | 569.598 | 14.294 | 569.029 | 62.1685
112.835 | 0.11056 | 16.7422 | 21.2604 | 31.9424 | 3.4863 | 27.9365 | 434.351 | 33.6473 | 34.0165 | 43.857 | 40.4411 | 57.7968 | 12.7285 | 76.856 | 10.442 | 88.2288 | 187.326 | 125.453 | 10.9994 | 153.229 | 29.4545 | 197.736 | 31.4012 | 272.307 | 14.5101 | 370.529 | 15.1476 | 425.358 | 35.5822 | 560.557 | 16.9937 | 559.437 | 83.9188
104.056 | 0.12379 | 16.5095 | 26.9194 | 30.8129 | 3.9112 | 27.8807 | 602.961 | 33.4126 | 43.3301 | 43.6819 | 50.5442 | 55.9766 | 15.9721 | 75.3342 | 12.1319 | 86.6549 | 340.989 | 121.989 | 14.1094 | 150.194 | 38.2386 | 192.468 | 44.5159 | 266.915 | 17.7227 | 361.38 | 18.9129 | 418.606 | 48.1272 | 551.108 | 20.5086 | 551.66 | 114.875
94.2484 | 0.14253 | 16.2312 | 33.4431 | 29.4865 | 4.4453 | 27.8807 | 602.961 | 33.0802 | 55.0283 | 43.6819 | 64.8352 | 54.8134 | 20.6114 | 73.7687 | 14.1801 | 85.5357 | 502.629 | 118.977 | 17.0789 | 148.106 | 50.2418 | 188.657 | 60.5124 | 260.846 | 22.4849 | 352.811 | 24.309 | 410.728 | 69.2587 | 538.039 | 25.8638 | 543.99 | 150.935
88.0525 | 0.15768 | 16.0857 | 127.338 | 28.3587 | 5.002 | 27.8807 | 602.961 | 32.7838 | 74.3548 | 43.5511 | 87.3436 | 54.2137 | 25.4533 | 72.3803 | 16.8246 | 85.1091 | 601.155 | 116.855 | 21.0068 | 146.633 | 63.6786 | 185.477 | 83.5002 | 253.644 | 28.6985 | 344.444 | 32.7154 | 407.048 | 100.972 | 526.331 | 33.2431 | 539.656 | 195.948
81.3641 | 0.18084 | 16.0215 | 602.359 | 26.9217 | 5.8641 | 27.8807 | 602.961 | 32.5877 | 103.736 | 43.5511 | 202.725 | 54.0513 | 46.5184 | 70.8761 | 20.4267 | 85.1091 | 601.155 | 115.23 | 25.8897 | 145.028 | 86.1293 | 182.716 | 110.924 | 246.887 | 37.7825 | 336.612 | 42.218 | 402.595 | 150.633 | 515.909 | 45.4607 | 532.685 | 269.846
74.6592 | 0.20739 | 16.0215 | 602.359 | 25.8403 | 6.7385 | 27.8807 | 602.961 | 32.5226 | 138.635 | 43.464 | 310.707 | 53.9973 | 33.6108 | 69.4727 | 25.9935 | 85.1091 | 601.155 | 113.969 | 32.0035 | 143.155 | 121.492 | 179.815 | 152.452 | 239.83 | 51.2568 | 329.947 | 60.2708 | 396.601 | 227.204 | 502.166 | 63.8699 | 526.858 | 378.362
68.5069 | 0.23879 | 16.0215 | 602.359 | 25.0015 | 7.7279 | 27.8807 | 602.961 | 32.3927 | 281.984 | 43.2905 | 440.034 | 53.9433 | 68.7068 | 68.37 | 32.8137 | 85.1091 | 601.155 | 112.61 | 42.0916 | 141.589 | 171.545 | 178.561 | 211.632 | 233.675 | 69.1895 | 325.034 | 85.9572 | 393.048 | 343.728 | 490.748 | 90.9081 | 522.138 | 508.189
63.684 | 0.2687 | 16.0215 | 602.359 | 24.2625 | 8.8096 | 27.8807 | 602.961 | 32.3604 | 404.581 | 43.0316 | 586.313 | 53.7817 | 259.265 | 67.4195 | 42.8561 | 85.1091 | 601.155 | 111.601 | 53.5089 | 141.306 | 247.114 | 176.431 | 312.577 | 227.223 | 104.569 | 320.195 | 121.857 | 390.697 | 482.438 | 481.031 | 126.071 | 520.053 | 591.022
57.7968 | 0.31595 | 16.0215 | 602.359 | 23.6162 | 10.2455 | 27.8807 | 602.961 | 32.328 | 521.054 | 43.0316 | 586.313 | 53.6206 | 601.155 | 66.8823 | 56.9315 | 85.1091 | 601.155 | 110.712 | 67.6839 | 141.024 | 360.269 | 175.025 | 477.16 | 223.84 | 145.162 | 317.009 | 600.554 | 388.359 | 600.554 | 471.506 | 172.578 | 520.053 | 591.022
51.0055 | 0.38823 | 16.0215 | 602.359 | 22.9183 | 12.4018 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 66.4157 | 79.6665 | 85.1091 | 601.155 | 110.38 | 89.4652 | 140.602 | 514.838 | 174.501 | 601.155 | 218.313 | 210.998 | 317.009 | 600.554 | 388.359 | 600.554 | 462.169 | 247.609 | 520.053 | 591.022
45.8298 | 0.46619 | 16.0215 | 602.359 | 22.4869 | 14.7588 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 65.2962 | 118.019 | 85.1091 | 601.155 | 109.063 | 113.165 | 140.18 | 602.359 | 174.501 | 601.155 | 215.709 | 297.332 | 317.009 | 600.554 | 388.359 | 600.554 | 455.288 | 372.357 | 520.053 | 591.022
40.2027 | 0.58557 | 16.0215 | 602.359 | 22.2854 | 17.4065 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 65.2309 | 168.317 | 85.1091 | 601.155 | 108.628 | 147.061 | 140.18 | 602.359 | 174.501 | 601.155 | 213.136 | 442.24 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
35.8712 | 0.71594 | 16.0215 | 602.359 | 22.2187 | 21.8859 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 65.0355 | 485.341 | 85.1091 | 601.155 | 108.411 | 204.353 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
32.0704 | 0.88767 | 16.0215 | 602.359 | 22.1743 | 33.4097 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 108.303 | 293.786 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
29.2224 | 1.0638 | 16.0215 | 602.359 | 22.1743 | 27.1899 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.655 | 407.423 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
26.257 | 1.3032 | 16.0215 | 602.359 | 22.1743 | 41.0934 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
24.1415 | 1.5432 | 16.0215 | 602.359 | 22.1521 | 52.1878 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
22.1079 | 1.8531 | 16.0215 | 602.359 | 22.0416 | 71.1542 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
20.5926 | 2.1659 | 16.0215 | 602.359 | 21.8005 | 94.5236 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
19.2004 | 2.5545 | 16.0215 | 602.359 | 21.7352 | 133.066 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
18.1004 | 2.9649 | 16.0215 | 602.359 | 21.6268 | 219.609 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
17.3039 | 3.3429 | 16.0215 | 602.359 | 21.562 | 363.526 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
16.493 | 3.7918 | 16.0215 | 602.359 | 21.4116 | 601.155 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
15.626 | 4.4497 | 16.0215 | 602.359 | 21.4116 | 601.155 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
14.849 | 5.1958 | 16.0215 | 602.359 | 21.4116 | 601.155 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
14.281 | 6.0912 | 16.0215 | 602.359 | 21.4116 | 601.155 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
13.7623 | 6.9368 | 16.0215 | 602.359 | 21.4116 | 601.155 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
13.3957 | 7.7978 | 16.0215 | 602.359 | 21.4116 | 601.155 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
13.0911 | 8.6352 | 16.0215 | 602.359 | 21.4116 | 601.155 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
12.8319 | 9.5912 | 16.0215 | 602.359 | 21.4116 | 601.155 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
12.5652 | 10.7386 | 16.0215 | 602.359 | 21.4116 | 601.155 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
12.3781 | 12.2907 | 16.0215 | 602.359 | 21.4116 | 601.155 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
12.1939 | 14.0672 | 16.0215 | 602.359 | 21.4116 | 601.155 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
12.0725 | 16.3764 | 16.0215 | 602.359 | 21.4116 | 601.155 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
11.9285 | 18.7998 | 16.0215 | 602.359 | 21.4116 | 601.155 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
11.798 | 25.6577 | 16.0215 | 602.359 | 21.4116 | 601.155 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
11.7862 | 74.2063 | 16.0215 | 602.359 | 21.4116 | 601.155 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
11.7745 | 293.492 | 16.0215 | 602.359 | 21.4116 | 601.155 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
11.7392 | 592.798 | 16.0215 | 602.359 | 21.4116 | 601.155 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
11.7392 | 592.798 | 16.0215 | 602.359 | 21.4116 | 601.155 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
11.7392 | 592.798 | 16.0215 | 602.359 | 21.4116 | 601.155 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
11.7392 | 592.798 | 16.0215 | 602.359 | 21.4116 | 601.155 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022
11.7392 | 592.798 | 16.0215 | 602.359 | 21.4116 | 601.155 | 27.8807 | 602.961 | 32.2957 | 601.757 | 43.0316 | 586.313 | 53.6206 | 601.155 | 64.9705 | 595.769 | 85.1091 | 601.155 | 107.118 | 601.155 | 140.18 | 602.359 | 174.501 | 601.155 | 212.285 | 601.155 | 317.009 | 600.554 | 388.359 | 600.554 | 451.209 | 601.757 | 520.053 | 591.022