## 165-2
S&C Power Fuses - Type SMU-20 (7.2 and 14.4 kV) | [9 empty] | S&C Power Fuses - Type SMU-20 (7.2 and 14.4 kV) | [9 empty] | S&C Power Fuses - Type SMU-20 (7.2 and 14.4 kV) | [9 empty] | S&C Power Fuses - Type SMU-20 (7.2 and 14.4 kV)
"K" Speed (TCC 165-2) | [9 empty] | "K" Speed (TCC 165-2) | [9 empty] | "K" Speed (TCC 165-2) | [9 empty] | "K" Speed (TCC 165-2)
Minimum Melting Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated August 29, 1988
Tolerance in Terms of Current: |  |  | Plus 10% for fuse units rated 6K through 200K | [6 empty] | Tolerance in Terms of Current: |  |  | Plus 10% for fuse units rated 6K through 200K | [6 empty] | Tolerance in Terms of Current: |  |  | Plus 10% for fuse units rated 6K through 200K | [6 empty] | Tolerance in Terms of Current: |  | Plus 10% for fuse units rated 6K through 200K
|  |  | Plus 20% for fuse units rated 3K | [9 empty] | Plus 20% for fuse units rated 3K | [9 empty] | Plus 20% for fuse units rated 3K | [8 empty] | Plus 20% for fuse units rated 3K
3K |  | 6K |  | 8K |  | 10K |  | 12K |  | 15K |  | 20K |  | 25K |  | 30K |  | 40K |  | 50K |  | 65K |  | 80K |  | 100K |  | 140K |  | 200K
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
5.9831 | 602.3588 | 13.1043 | 601.1553 | 16.4107 | 602.3588 | 20.49 | 604.7734 | 27.274 | 612.6865 | 33.2793 | 605.3782 | 42.6887 | 602.3588 | 54.0513 | 601.1553 | 67.2848 | 598.7557 | 80.0726 | 603.5646 | 109.3916 | 604.1687 | 132.414 | 594.579 | 165.825 | 593.9845 | 202.7417 | 601.1553 | 319.7102 | 592.1046 | 524.2307 | 602.3588
5.9771 | 375.723 | 13.1305 | 297.6304 | 16.4107 | 384.465 | 20.49 | 424.4749 | 27.1923 | 358.8314 | 33.4127 | 335.2417 | 42.817 | 390.2752 | 54.54 | 280.2976 | 67.7574 | 384.0806 | 80.3132 | 465.3793 | 110.3805 | 332.2381 | 133.7448 | 362.8002 | 166.157 | 394.1977 | 203.758 | 338.611 | 321.7266 | 527.4389 | 538.5776 | 436.965
5.9532 | 196.7337 | 13.1043 | 150.483 | 16.526 | 239.5714 | 20.5515 | 245.3907 | 27.138 | 215.261 | 33.3793 | 184.5371 | 43.1609 | 227.6596 | 54.9231 | 150.483 | 68.2334 | 259.5245 | 81.0393 | 284.5338 | 111.2671 | 189.398 | 134.9539 | 236.0045 | 166.823 | 235.7688 | 206.0116 | 179.6214 | 327.8525 | 343.3577 | 554.9796 | 297.6304
5.9771 | 105.0935 | 13.1043 | 92.9302 | 16.5757 | 142.2876 | 20.6752 | 138.9133 | 27.138 | 124.6924 | 33.3793 | 102.9094 | 43.5511 | 121.6137 | 55.3643 | 78.6375 | 68.8503 | 172.7509 | 81.6085 | 173.0967 | 112.1608 | 115.4514 | 136.0379 | 152.1476 | 169.5136 | 126.9572 | 209.1252 | 118.4925 | 335.8501 | 220.0564 | 571.3099 | 207.8572
6.0311 | 59.9103 | 13.1043 | 55.2489 | 16.6588 | 80.5477 | 20.7166 | 81.1946 | 27.2196 | 78.089 | 33.4461 | 62.6679 | 44.0328 | 60.3312 | 55.9766 | 43.5909 | 68.9881 | 112.4884 | 82.264 | 106.3622 | 112.9487 | 73.984 | 137.5426 | 92.5593 | 172.42 | 76.2372 | 213.1365 | 68.9133 | 346.5758 | 130.4322 | 587.5325 | 145.0169
6.153 | 37.7826 | 13.1305 | 33.4097 | 16.7423 | 46.3327 | 20.7788 | 47.2687 | 27.1923 | 46.9859 | 33.2793 | 40.8476 | 44.7878 | 41.9235 | 57.279 | 25.4533 | 69.6814 | 69.6058 | 82.9248 | 70.5872 | 114.198 | 51.8756 | 138.9249 | 61.3655 | 176.2552 | 43.941 | 217.4421 | 46.3327 | 361.4112 | 73.4621 | 610.2885 | 90.0937
6.3151 | 26.0977 | 13.1568 | 21.0699 | 16.8094 | 30.8719 | 20.7996 | 29.8997 | 27.1923 | 29.8399 | 33.7485 | 29.016 | 45.4192 | 27.767 | 59.4975 | 15.5622 | 70.4522 | 45.6429 | 84.939 | 43.4168 | 115.9238 | 35.6535 | 141.4482 | 44.1171 | 182.1687 | 28.1303 | 223.393 | 33.0112 | 381.2512 | 39.2343 | 630.7639 | 57.2168
6.5728 | 16.624 | 13.3824 | 13.4213 | 16.9613 | 20.4677 | 20.9039 | 20.6734 | 27.2468 | 22.6429 | 34.3271 | 20.9439 | 46.3367 | 19.1604 | 61.6168 | 10.463 | 71.7318 | 29.4251 | 87.0022 | 28.4699 | 117.5582 | 26.8925 | 144.7392 | 32.0036 | 188.0923 | 19.7637 | 229.7365 | 24.3577 | 403.8693 | 22.3523 | 654.5391 | 38.2004
6.8684 | 11.4026 | 13.6254 | 10.6211 | 17.2694 | 14.6706 | 21.3689 | 16.1004 | 27.6033 | 18.7998 | 35.3725 | 13.9831 | 47.5573 | 14.237 | 64.0033 | 7.9872 | 73.7687 | 19.7835 | 89.7415 | 18.2259 | 119.5738 | 20.5086 | 148.9981 | 21.9079 | 194.987 | 13.9691 | 238.1576 | 17.1474 | 435.063 | 12.4458 | 675.1477 | 26.8119
7.2062 | 8.6785 | 14.1249 | 8.0433 | 17.6535 | 11.7734 | 21.8661 | 12.6271 | 28.1891 | 14.7147 | 36.4498 | 10.6211 | 48.81 | 10.7064 | 66.5487 | 6.2267 | 76.3199 | 12.5015 | 92.5671 | 13.3811 | 121.7456 | 15.7974 | 153.0758 | 16.5411 | 203.758 | 9.9428 | 248.8705 | 12.3277 | 474.5963 | 7.4931 | 708.3451 | 18.3723
7.5078 | 6.9507 | 14.716 | 6.2267 | 18.2458 | 8.9876 | 22.487 | 10.2763 | 29.1349 | 11.2441 | 37.8994 | 8.1404 | 51.0056 | 8.0594 | 69.821 | 4.7771 | 78.4871 | 9.2428 | 96.731 | 9.8438 | 124.5782 | 12.1077 | 157.7376 | 12.2294 | 212.7106 | 7.8056 | 261.3688 | 8.8715 | 528.6867 | 4.5348 | 741.69 | 12.9209
7.822 | 5.829 | 15.5792 | 4.6406 | 18.9336 | 7.2271 | 23.3112 | 8.3049 | 30.233 | 8.5236 | 39.9622 | 6.1034 | 53.3532 | 6.3271 | 73.4742 | 3.8723 | 80.3936 | 7.4996 | 101.5889 | 7.4622 | 127.3492 | 9.8242 | 161.5691 | 9.7654 | 223.1697 | 6.0487 | 273.9464 | 6.8131 | 622.5755 | 2.4219 | 777.3816 | 9.3544
8.3473 | 4.6825 | 16.5757 | 3.5108 | 19.6866 | 5.8582 | 24.2141 | 6.8199 | 31.8786 | 6.3208 | 42.1795 | 4.7771 | 56.9364 | 4.7533 | 78.7229 | 3.0218 | 83.2571 | 6.1647 | 106.7974 | 5.829 | 132.2816 | 7.329 | 166.3232 | 8.0594 | 237.2068 | 4.599 | 288.5685 | 5.3007 | 746.3148 | 1.437 | 818.8749 | 6.5329
9.0788 | 3.713 | 17.3386 | 2.912 | 20.6545 | 4.6779 | 25.4047 | 5.3647 | 33.2128 | 5.098 | 43.9009 | 3.9663 | 60.3967 | 3.7541 | 85.6213 | 2.293 | 87.0893 | 4.997 | 112.1608 | 4.7724 | 137.1305 | 5.8407 | 172.42 | 6.5003 | 252.127 | 3.5674 | 306.1064 | 4.0994 | 882.5432 | 0.94431 | 860.8593 | 4.997
9.9935 | 2.9325 | 18.2458 | 2.3841 | 22.2632 | 3.5108 | 26.4415 | 4.4676 | 34.9506 | 4.0546 | 46.1979 | 3.2539 | 65.3616 | 2.8288 | 93.1242 | 1.7947 | 92.8452 | 3.8146 | 120.1731 | 3.7842 | 142.7269 | 4.7438 | 179.9957 | 5.1906 | 269.8679 | 2.8344 | 324.3854 | 3.3934 | 1001.847 | 0.70097 | 916.8384 | 3.7956
10.9785 | 2.3393 | 19.143 | 1.9974 | 24.0212 | 2.7728 | 28.1046 | 3.4759 | 37.2978 | 3.1767 | 48.5665 | 2.7315 | 69.6814 | 2.2861 | 102.9181 | 1.3755 | 100.1765 | 2.9033 | 133.2109 | 2.7562 | 149.5953 | 3.919 | 189.0351 | 4.2497 | 290.0149 | 2.2566 | 347.2108 | 2.7397 | 1176.061 | 0.49703 | 996.183 | 2.7867
12.4901 | 1.7382 | 20.883 | 1.5202 | 26.4151 | 2.0935 | 29.7234 | 2.8975 | 41.2205 | 2.4081 | 50.9546 | 2.3323 | 74.0643 | 1.9057 | 112.4978 | 1.0875 | 105.5235 | 2.4226 | 147.2207 | 2.0789 | 158.2116 | 3.2441 | 204.5746 | 3.303 | 312.2901 | 1.8237 | 366.8424 | 2.3323 | 1421.676 | 0.33628 | 1091.089 | 2.0872
13.9843 | 1.3349 | 23.8775 | 1.0799 | 29.7234 | 1.5126 | 31.9105 | 2.3675 | 46.2441 | 1.7574 | 54.3223 | 1.9384 | 78.1737 | 1.637 | 121.8674 | 0.88678 | 112.8358 | 1.9618 | 168.3311 | 1.4916 | 172.938 | 2.4691 | 221.3915 | 2.5827 | 334.9336 | 1.5096 | 395.4135 | 1.8962 | 1736.691 | 0.22681 | 1184.328 | 1.6584
16.1341 | 0.96932 | 27.4656 | 0.77557 | 32.4901 | 1.1934 | 35.0907 | 1.842 | 52.2968 | 1.289 | 58.4361 | 1.5854 | 86.4818 | 1.28 | 132.5464 | 0.72821 | 121.5023 | 1.5822 | 201.9323 | 0.95968 | 186.2208 | 2.0154 | 240.3107 | 2.0316 | 366.4756 | 1.2298 | 431.7868 | 1.5021 | 2112.631 | 0.15441 | 1280.403 | 1.3335
18.0823 | 0.75189 | 33.3793 | 0.4965 | 37.0006 | 0.85201 | 38.8588 | 1.4174 | 57.9126 | 1.0069 | 62.3606 | 1.3416 | 97.508 | 0.97223 | 150.0447 | 0.55646 | 134.6843 | 1.22 | 229.0482 | 0.72967 | 206.8374 | 1.5463 | 263.7317 | 1.6126 | 404.209 | 0.96932 | 485.3798 | 1.1284 | 2610.666 | 0.10073 | 1440.766 | 0.98693
20.347 | 0.58616 | 37.7481 | 0.376 | 41.51 | 0.65366 | 42.9027 | 1.0962 | 66.8154 | 0.72676 | 66.2168 | 1.1489 | 108.9548 | 0.75869 | 174.8508 | 0.40895 | 151.7043 | 0.92852 | 271.7636 | 0.5035 | 236.4963 | 1.1105 | 294.9873 | 1.2224 | 453.9249 | 0.75039 | 560.5574 | 0.80722 | 3343.119 | 0.061666 | 1673.932 | 0.68649
23.3112 | 0.43773 | 45.6469 | 0.25103 | 46.3367 | 0.50958 | 47.9392 | 0.8343 | 79.0384 | 0.50857 | 70.4522 | 0.99088 | 120.6548 | 0.60462 | 212.2857 | 0.27911 | 174.6761 | 0.6756 | 314.4838 | 0.3704 | 262.4165 | 0.85542 | 320.516 | 0.99784 | 507.7208 | 0.59442 | 642.8627 | 0.60886 | 4285.561 | 0.037398 | 1900.61 | 0.50552
26.2571 | 0.33988 | 56.5958 | 0.16346 | 51.3125 | 0.40448 | 52.6641 | 0.66887 | 92.3821 | 0.3609 | 74.8835 | 0.86835 | 131.7536 | 0.502 | 267.9854 | 0.1769 | 201.9323 | 0.49206 | 377.2591 | 0.25255 | 299.745 | 0.62553 | 341.6997 | 0.85713 | 584.6021 | 0.44301 | 732.1104 | 0.46248 | 5137.333 | 0.02597 | 2179.673 | 0.37077
30.5064 | 0.24705 | 71.5885 | 0.10196 | 59.6166 | 0.29342 | 60.3967 | 0.4896 | 110.16 | 0.24879 | 79.1966 | 0.76708 | 146.6331 | 0.40367 | 344.1 | 0.10805 | 252.127 | 0.31564 | 470.0937 | 0.16265 | 347.906 | 0.45559 | 375.3775 | 0.68581 | 674.473 | 0.33017 | 861.7205 | 0.32951 | 6321.862 | 0.017101 | 2568.121 | 0.26233
35.9071 | 0.18011 | 90.9158 | 0.063408 | 68.3017 | 0.22043 | 69.3339 | 0.35874 | 132.6791 | 0.17082 | 92.2898 | 0.55813 | 173.111 | 0.29079 | 471.0348 | 0.058008 | 318.5988 | 0.19727 | 610.2885 | 0.096794 | 393.4413 | 0.34918 | 404.209 | 0.58091 | 817.2385 | 0.22332 | 1085.646 | 0.20553 | 7554.571 | 0.012038 | 3062.325 | 0.18156
43.2041 | 0.12466 | 118.2656 | 0.03736 | 76.6258 | 0.17444 | 77.5508 | 0.28248 | 166.3232 | 0.10892 | 111.3784 | 0.38552 | 219.408 | 0.1812 | 637.7404 | 0.031931 | 417.7704 | 0.11473 | 803.4631 | 0.055678 | 452.5652 | 0.26285 | 438.3124 | 0.48862 | 1038.914 | 0.13888 | 1355.507 | 0.13131 | 8310.417 | 0.01001 | 3736.592 | 0.12001
53.4066 | 0.081662 | 164.5037 | 0.019367 | 90.9158 | 0.12591 | 92.7524 | 0.19747 | 210.5942 | 0.067666 | 138.786 | 0.24953 | 279.4805 | 0.11167 | 871.2519 | 0.017246 | 519.5338 | 0.074336 | 1097.654 | 0.029982 | 573.0262 | 0.16494 | 519.5338 | 0.34022 | 1301.055 | 0.088729 | 1743.989 | 0.079169 |  |  | 4788.292 | 0.073522
62.8615 | 0.059121 | 228.5906 | 0.01 | 104.6827 | 0.095258 | 108.6285 | 0.14411 | 262.4165 | 0.043667 | 166.4896 | 0.17288 | 348.2541 | 0.072428 | 1148.177 | 0.01 | 676.4993 | 0.043842 | 1468.403 | 0.016703 | 693.625 | 0.11291 | 637.1031 | 0.22109 | 1759.756 | 0.048598 | 2298.312 | 0.045631 |  |  | 6216.291 | 0.043536
75.6362 | 0.04096 |  |  | 126.0821 | 0.066062 | 127.4767 | 0.10454 | 327.9734 | 0.027843 | 197.736 | 0.12244 | 433.5175 | 0.046693 |  |  | 965.775 | 0.021404 | 1893.023 | 0.01 | 829.5898 | 0.078617 | 811.5379 | 0.13599 | 2330.714 | 0.02776 | 2956.997 | 0.027401 |  |  | 7957.964 | 0.026591
93.4974 | 0.026885 |  |  | 156.0121 | 0.043667 | 157.7376 | 0.06862 | 416.519 | 0.017246 | 238.3959 | 0.084065 | 543.9906 | 0.029892 |  |  | 1416.481 | 0.01 |  |  | 984.3002 | 0.055901 | 1022.423 | 0.08508 | 3124.188 | 0.015434 | 3729.127 | 0.017333 |  |  | 10208.01 | 0.016128
117.9114 | 0.016955 |  |  | 196.3567 | 0.027649 | 205.3946 | 0.040633 | 544.5348 | 0.01 | 296.7626 | 0.054195 | 706.9299 | 0.017524 | [6 empty] | 1165.529 | 0.040028 | 1358.22 | 0.048163 | 3885.198 | 0.01 | 4889.91 | 0.01 |  |  | 12976.92 | 0.01
153.997 | 0.01 |  |  | 250.8695 | 0.017057 | 278.3647 | 0.022389 |  |  | 388.3597 | 0.031614 | 934.4245 | 0.01 | [6 empty] | 1413.65 | 0.027101 | 1802.501 | 0.027401
|  |  |  | 326.9908 | 0.01 | 417.7704 | 0.01 |  |  | 504.1792 | 0.018814 | [8 empty] | 1795.305 | 0.016787 | 2440.431 | 0.014963
[10 empty] | 692.9318 | 0.01 | [8 empty] | 2326.057 | 0.01 | 2995.689 | 0.01