## 450-8
S&C Fault Tamer Fuse Limiter | [9 empty] | S&C Fault Tamer Fuse Limiter
15-38 kV System Voltages (TCC 450-8) | [9 empty] | 15-38 kV System Voltages (TCC 450-8)
Minimum Melting Time-Current Characteristic Curves Dated March 19, 2007 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated March 19, 2007
Tolerance in Terms of Current: Plus 10% | [9 empty] | Tolerance in Terms of Current: Plus 10%
20A |  | 15A |  | 10A |  | 7A |  | 5A |  | 3A
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
40.0517 | 300 | 30.008 | 300 | 20.0148 | 300 | 14.0558 | 300 | 9.979 | 300 | 6.0038 | 300
40.2126 | 212.6771 | 29.9908 | 238.5826 | 20.0952 | 245.222 | 14.1123 | 243.2666 | 10.0651 | 250.7524 | 6.1359 | 256.4074
40.5364 | 143.9125 | 30.1286 | 158.7869 | 20.3151 | 166.4099 | 14.2422 | 180.1771 | 10.1986 | 193.7492 | 6.5424 | 183.19
41.381 | 90.1466 | 30.2496 | 96.9371 | 21.0496 | 85.0876 | 14.4642 | 128.5067 | 10.3992 | 148.6807 | 7.004 | 140.417
42.3158 | 57.3464 | 30.7739 | 57.052 | 21.8857 | 55.4438 | 14.9957 | 91.0273 | 10.6341 | 122.9007 | 7.6499 | 103.1715
43.4955 | 33.751 | 31.9231 | 34.9491 | 22.5862 | 42.6687 | 15.5646 | 73.2067 | 11.0565 | 96.9925 | 8.5785 | 74.9862
45.509 | 19.6045 | 33.3627 | 23.6085 | 23.9315 | 30.5195 | 16.5485 | 58.3387 | 11.5949 | 79.2631 | 10.3813 | 50.2502
47.4524 | 12.951 | 36.2937 | 14.0626 | 25.9001 | 22.8123 | 18.2411 | 44.2846 | 12.2996 | 64.7005 | 12.8616 | 34.2762
49.6491 | 9.2634 | 38.7206 | 10.9782 | 28.7296 | 16.159 | 19.7529 | 36.2311 | 13.5654 | 50.078 | 14.6225 | 27.5186
51.3852 | 7.5745 | 41.7142 | 8.3765 | 32.0146 | 11.558 | 21.7981 | 29.9147 | 14.9357 | 39.6571 | 17.2947 | 20.949
52.0071 | 7.0037 | 45.1714 | 6.4982 | 43.9463 | 5.1548 | 24.9535 | 23.2601 | 17.424 | 29.0882 | 20.0952 | 16.7613
53.4263 | 6.0569 | 50.0489 | 4.7501 | 52.727 | 3.3995 | 28.4349 | 18.5573 | 19.7982 | 22.9693 | 23.2958 | 13.5108
54.8842 | 5.3043 | 52.1264 | 4.2246 | 62.3984 | 2.3321 | 33.3818 | 14.487 | 22.8989 | 17.8495 | 26.6526 | 11.1363
56.8034 | 4.5611 | 59.0597 | 3.0373 | 78.8269 | 1.4124 | 38.8762 | 11.4004 | 26.6221 | 13.9664 | 33.9215 | 7.9608
57.987 | 4.2005 | 69.8126 | 1.9544 | 117.7114 | 0.599 | 46.1919 | 8.8038 | 32.7754 | 10.0527 | 42.828 | 5.8292
62.0065 | 3.2179 | 82.005 | 1.3308 | 126.2319 | 0.51125 | 51.3558 | 7.5658 | 38.6542 | 7.8389 | 50.3653 | 4.6746
67.6862 | 2.4149 | 96.3267 | 0.92401 | 148.8734 | 0.36235 | 52.0071 | 7.0037 | 48.3303 | 5.6974 | 52.1264 | 4.2246
74.9948 | 1.802 | 117.7114 | 0.599 | 180.1605 | 0.24435 | 53.4263 | 6.0569 | 56.8034 | 4.5559 | 59.0597 | 3.0373
88.5475 | 1.1749 | 126.2319 | 0.51125 | 236.9054 | 0.14104 | 54.8842 | 5.3043 | 57.987 | 4.2005 | 69.8126 | 1.9544
111.2217 | 0.67814 | 148.8734 | 0.36235 | 327.4417 | 0.074721 | 56.8034 | 4.5611 | 62.0065 | 3.2179 | 82.005 | 1.3308
117.7114 | 0.599 | 180.1605 | 0.24435 | 514.8345 | 0.030551 | 57.987 | 4.2005 | 67.6862 | 2.4149 | 96.3267 | 0.92401
126.2319 | 0.51125 | 236.9054 | 0.14104 | 647.0377 | 0.019535 | 62.0065 | 3.2179 | 74.9948 | 1.802 | 117.7114 | 0.599
148.8734 | 0.36235 | 327.4417 | 0.074721 | 895.8491 | 0.01 | 67.6862 | 2.4149 | 88.5475 | 1.1749 | 126.2319 | 0.51125
180.1605 | 0.24435 | 514.8345 | 0.030551 |  |  | 74.9948 | 1.802 | 111.2217 | 0.67814 | 148.8734 | 0.36235
236.9054 | 0.14104 | 647.0377 | 0.019535 |  |  | 88.5475 | 1.1749 | 117.7114 | 0.599 | 180.1605 | 0.24435
327.4417 | 0.074721 | 895.8491 | 0.01 |  |  | 111.2217 | 0.67814 | 126.2319 | 0.51125 | 236.9054 | 0.14104
514.8345 | 0.030551 |  |  |  |  | 117.7114 | 0.599 | 148.8734 | 0.36235 | 327.4417 | 0.074721
647.0377 | 0.019535 |  |  |  |  | 126.2319 | 0.51125 | 180.1605 | 0.24435 | 514.8345 | 0.030551
895.8491 | 0.01 |  |  |  |  | 148.8734 | 0.36235 | 236.9054 | 0.14104 | 647.0377 | 0.019535
[6 empty] | 180.1605 | 0.24435 | 327.4417 | 0.074721 | 895.8491 | 0.01
[6 empty] | 236.9054 | 0.14104 | 514.8345 | 0.030551
[6 empty] | 327.4417 | 0.074721 | 647.0377 | 0.019535
[6 empty] | 514.8345 | 0.030551 | 895.8491 | 0.01
[6 empty] | 647.0377 | 0.019535
[6 empty] | 895.8491 | 0.01