## 119_22
S&C Power Fuses - Type SMU-20 (7.2 and 14.4 kV) | [9 empty] | S&C Power Fuses - Type SMU-20 (7.2 and 14.4 kV) | [9 empty] | S&C Power Fuses - Type SMU-20 (7.2 and 14.4 kV)
Slow Speed (TCC 119-2-2) | [9 empty] | Slow Speed (TCC 119-2-2) | [9 empty] | Slow Speed (TCC 119-2-2)
Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
18470.4 | 0.016504 | 18451.9 | 0.016405 | 18396.7 | 0.016504 | 18415.1 | 0.016504 | 18451.9 | 0.016405 | 18451.9 | 0.016504 | 18451.9 | 0.016504 | 18488.9 | 0.016504 | 18674.7 | 0.016504 | 18600.1 | 0.016504 | 18618.8 | 0.016504 | 18470.4 | 0.016504 | 18378.3 | 0.025194
16186.4 | 0.016703 | 15598.4 | 0.016703 | 15881.7 | 0.016703 | 17118.7 | 0.016703 | 16513.4 | 0.016803 | 16398.2 | 0.017006 | 16830.1 | 0.016905 | 17016.3 | 0.017006 | 17447 | 0.016905 | 17118.7 | 0.017194 | 17170.1 | 0.017402 | 17640 | 0.017092 | 17799.5 | 0.0256
14356 | 0.016905 | 13412.3 | 0.017006 | 13332 | 0.017194 | 15443.2 | 0.017006 | 14213.2 | 0.017402 | 14852.5 | 0.017507 | 14837.7 | 0.017807 | 15443.2 | 0.017807 | 15993.3 | 0.0177 | 15676.6 | 0.018094 | 15692.3 | 0.018608 | 16762.9 | 0.017896 | 17101.6 | 0.026406
12770.9 | 0.017092 | 11236.5 | 0.017402 | 11824.4 | 0.017594 | 13015.9 | 0.0177 | 12099.6 | 0.018203 | 13506.5 | 0.018004 | 13751.8 | 0.018404 | 14399.1 | 0.018497 | 14822.8 | 0.018608 | 14284.4 | 0.019601 | 14356 | 0.019997 | 15739.4 | 0.018795 | 16283.8 | 0.027401
11270.3 | 0.017402 | 9394.95 | 0.017807 | 10015.8 | 0.018094 | 11440.6 | 0.018094 | 11091.4 | 0.018608 | 12669.1 | 0.018497 | 12770.9 | 0.019003 | 13398.9 | 0.019194 | 13479.5 | 0.019997 | 13199.4 | 0.021001 | 13533.5 | 0.021107 | 14852.5 | 0.019897 | 15320.2 | 0.028691
9985.88 | 0.0177 | 8126.84 | 0.018294 | 9062.75 | 0.018404 | 10208 | 0.018497 | 10218.2 | 0.019003 | 11349.4 | 0.019098 | 11742 | 0.019798 | 12282.4 | 0.020299 | 12160.2 | 0.021404 | 12393.5 | 0.02199 | 12809.3 | 0.022211 | 14199 | 0.020792 | 14399.1 | 0.030404
8918.9 | 0.018004 | 6925.24 | 0.018795 | 8021.88 | 0.018908 | 8821.33 | 0.019003 | 9126.41 | 0.019699 | 10393.4 | 0.019699 | 10582.1 | 0.020792 | 11113.6 | 0.021598 | 11270.3 | 0.022705 | 11636.8 | 0.02321 | 12051.3 | 0.023798 | 13278.8 | 0.022211 | 13398.9 | 0.032414
7942.06 | 0.018294 | 6008.49 | 0.019309 | 7121.89 | 0.019309 | 7645.92 | 0.019798 | 8192.12 | 0.020401 | 9413.76 | 0.020503 | 9565.59 | 0.021793 | 9965.93 | 0.023094 | 10383 | 0.023989 | 10645.8 | 0.024993 | 11102.5 | 0.026013 | 12631.2 | 0.023608 | 12656.5 | 0.034384
7043.98 | 0.018701 | 5244.46 | 0.019798 | 6191.47 | 0.019897 | 6541.54 | 0.020503 | 7251.24 | 0.021191 | 8291.02 | 0.02149 | 8672.64 | 0.023002 | 8786.12 | 0.024893 | 9153.83 | 0.026512 | 9546.48 | 0.027594 | 10414.2 | 0.027899 | 11730.2 | 0.0256 | 11848.1 | 0.036803
6129.87 | 0.019194 | 4263.85 | 0.020606 | 5377.23 | 0.020606 | 5778.67 | 0.021191 | 6172.93 | 0.022502 | 7449.69 | 0.022389 | 7792.59 | 0.024303 | 7722.77 | 0.02721 | 8143.11 | 0.029008 | 8690 | 0.030012 | 9671.4 | 0.030404 | 10904.4 | 0.028011 | 11058.2 | 0.03959
5431.27 | 0.019699 | 3529.56 | 0.021404 | 4688.78 | 0.021191 | 5003.68 | 0.0221 | 5302.47 | 0.023703 | 6574.33 | 0.023703 | 7107.66 | 0.025498 | 6870.06 | 0.029388 | 7294.88 | 0.031899 | 7808.19 | 0.033201 | 8945.7 | 0.033401 | 10015.8 | 0.030988 | 10228.4 | 0.043189
4875.26 | 0.020097 | 3044 | 0.022389 | 4019.56 | 0.02199 | 4446.75 | 0.023002 | 4495.93 | 0.024993 | 5972.54 | 0.024695 | 6450.6 | 0.026993 | 6105.4 | 0.031995 | 6528.47 | 0.035114 | 7215.08 | 0.036002 | 8175.75 | 0.037509 | 9035.6 | 0.035502 | 9264.34 | 0.048598
4263.85 | 0.020606 | 2670.25 | 0.023303 | 3360.78 | 0.023002 | 3885.19 | 0.024109 | 4051.85 | 0.026091 | 5366.48 | 0.026013 | 5936.82 | 0.028292 | 5436.7 | 0.034904 | 5755.6 | 0.039314 | 6700.44 | 0.038807 | 7494.53 | 0.042292 | 8332.58 | 0.039789 | 8517.92 | 0.053925
3633.41 | 0.021297 | 2445.31 | 0.023893 | 2980.74 | 0.023798 | 3411.57 | 0.025194 | 3747.81 | 0.026993 | 4943.99 | 0.026993 | 5469.42 | 0.029713 | 4870.38 | 0.038 | 5318.4 | 0.042504 | 6272.49 | 0.042207 | 6994.84 | 0.046506 | 7699.63 | 0.044504 | 7886.66 | 0.059477
3022.77 | 0.0221 | 2241.56 | 0.024596 | 2630.5 | 0.024596 | 3004.69 | 0.026512 | 3456.21 | 0.028011 | 4637.49 | 0.028011 | 5109.86 | 0.031112 | 4393.71 | 0.041496 | 4939.05 | 0.045585 | 5907.21 | 0.045403 | 6399.2 | 0.05291 | 6939.11 | 0.05181 | 7251.24 | 0.066726
2630.5 | 0.022705 | 2032.31 | 0.0256 | 2370.67 | 0.025498 | 2683.64 | 0.027899 | 3196.87 | 0.029096 | 4345.64 | 0.029008 | 4726.44 | 0.032609 | 3979.57 | 0.045087 | 4559.32 | 0.049978 | 5458.49 | 0.05038 | 5761.36 | 0.061781 | 6179.1 | 0.061781 | 6720.57 | 0.074336
2399.29 | 0.023094 | 1861.11 | 0.026512 | 2147.22 | 0.026512 | 2413.73 | 0.029212 | 2992.69 | 0.030192 | 4019.56 | 0.030404 | 4393.71 | 0.034315 | 3637.05 | 0.049087 | 4187.79 | 0.05529 | 5038.83 | 0.05652 | 5207.88 | 0.072067 | 5546.53 | 0.073522 | 6191.47 | 0.083312
2239.32 | 0.023608 | 1721.46 | 0.027594 | 1982.13 | 0.027401 | 2160.14 | 0.030988 | 2795.95 | 0.031393 | 3766.6 | 0.031614 | 4108.97 | 0.035895 | 3384.39 | 0.052804 | 3885.19 | 0.061227 | 4693.47 | 0.062777 | 4660.73 | 0.085763 | 4978.72 | 0.087496 | 5681.26 | 0.094783
2087.93 | 0.023989 | 1600.27 | 0.028491 | 1874.18 | 0.028011 | 1994.06 | 0.032511 | 2643.68 | 0.032707 | 3550.8 | 0.032904 | 3835.01 | 0.037811 | 3096.19 | 0.058008 | 3487.46 | 0.07071 | 4225.65 | 0.07367 | 4272.39 | 0.098159 | 4522.99 | 0.10268 | 5156.06 | 0.10957
1962.41 | 0.0244 | 1486.13 | 0.029713 | 1775.66 | 0.028691 | 1835.23 | 0.03411 | 2497.21 | 0.034008 | 3314.06 | 0.034695 | 3554.35 | 0.04031 | 2898.44 | 0.062277 | 3142.98 | 0.081989 | 3808.26 | 0.087234 | 3838.85 | 0.11752 | 4084.39 | 0.12268 | 4684.1 | 0.12807
1811.53 | 0.024993 | 1369.13 | 0.031393 | 1684 | 0.029506 | 1689.06 | 0.036292 | 2326.05 | 0.036002 | 3102.39 | 0.036401 | 3314.06 | 0.042802 | 2697.09 | 0.067802 | 2812.78 | 0.096794 | 3347.36 | 0.1073 | 3483.97 | 0.1386 | 3717.95 | 0.14541 | 4255.33 | 0.14969
1695.83 | 0.0256 | 1257.56 | 0.033301 | 1595.48 | 0.030587 | 1571.72 | 0.038191 | 2155.82 | 0.038305 | 2915.88 | 0.038382 | 3068.45 | 0.045722 | 2509.72 | 0.074336 | 2583.57 | 0.11056 | 2998.68 | 0.12871 | 3180.93 | 0.16297 | 3347.36 | 0.17725 | 3736.59 | 0.1843
1554.53 | 0.026406 | 1157.39 | 0.035609 | 1507.08 | 0.031709 | 1445.09 | 0.041083 | 2010.08 | 0.040919 | 2762.6 | 0.040189 | 2807.16 | 0.049481 | 2296.01 | 0.083562 | 2365.93 | 0.12769 | 2718.75 | 0.15165 | 2892.65 | 0.19414 | 2965.88 | 0.22043 | 3337.34 | 0.22624
1458.16 | 0.02721 | 1075.91 | 0.037886 | 1427.85 | 0.032904 | 1320.71 | 0.044594 | 1876.06 | 0.043798 | 2604.32 | 0.042504 | 2606.93 | 0.053122 | 2138.65 | 0.091982 | 2162.3 | 0.1482 | 2442.87 | 0.18302 | 2662.25 | 0.2276 | 2662.25 | 0.27086 | 2977.76 | 0.27966
1360.93 | 0.028011 | 990.224 | 0.041001 | 1332.65 | 0.034799 | 1196.23 | 0.049382 | 1749.22 | 0.047209 | 2479.79 | 0.044504 | 2406.5 | 0.057374 | 1952.62 | 0.10444 | 1896.81 | 0.18265 | 2221.48 | 0.21868 | 2469.89 | 0.26024 | 2307.52 | 0.35199 | 2667.58 | 0.34364
1267.66 | 0.028893 | 902.285 | 0.044907 | 1242.56 | 0.036803 | 1097.65 | 0.054685 | 1621.21 | 0.051397 | 2351.78 | 0.047115 | 2201.57 | 0.063218 | 1788.13 | 0.11953 | 1652.31 | 0.23243 | 1994.06 | 0.26682 | 2284.56 | 0.29994 | 2056.84 | 0.43598 | 2442.87 | 0.40977
1196.23 | 0.029713 | 833.748 | 0.048989 | 1155.08 | 0.039314 | 1016.3 | 0.060315 | 1511.61 | 0.056182 | 2228.15 | 0.049878 | 2058.9 | 0.068278 | 1629.34 | 0.1386 | 1458.16 | 0.29224 | 1826.08 | 0.31344 | 2127.98 | 0.33988 | 1791.71 | 0.56543 | 2162.3 | 0.52826
1127.69 | 0.030802 | 754.406 | 0.054794 | 1072.69 | 0.042504 | 922.356 | 0.068895 | 1415.06 | 0.061288 | 2111.02 | 0.05291 | 1925.47 | 0.074484 | 1492.08 | 0.16039 | 1265.13 | 0.3813 | 1652.31 | 0.37713 | 1960.45 | 0.39806 | 1617.97 | 0.68581 | 1935.13 | 0.66156
1065.21 | 0.031899 | 694.319 | 0.060922 | 983.316 | 0.046413 | 835.417 | 0.079566 | 1306.26 | 0.068415 | 1942.88 | 0.058008 | 1773.89 | 0.082979 | 1360.93 | 0.18859 | 1110.9 | 0.49206 | 1475.76 | 0.46712 | 1777.44 | 0.48087 | 1462.54 | 0.84016 | 1800.69 | 0.77479
977.434 | 0.033804 | 630.133 | 0.068689 | 898.683 | 0.051603 | 711.895 | 0.10044 | 1191.45 | 0.077991 | 1831.57 | 0.062028 | 1600.27 | 0.096119 | 1226.51 | 0.22715 | 966.741 | 0.65106 | 1291.97 | 0.60583 | 1624.45 | 0.57055 | 1294.56 | 1.0745 | 1622.83 | 0.97223
903.188 | 0.036111 | 571.309 | 0.078539 | 796.264 | 0.060075 | 611.51 | 0.12731 | 1086.73 | 0.089442 | 1711.16 | 0.067734 | 1413.65 | 0.116 | 1118.7 | 0.26951 | 869.511 | 0.81045 | 1152.77 | 0.75793 | 1472.81 | 0.6927 | 1179.6 | 1.3362 | 1493.57 | 1.1698
848.891 | 0.037886 | 514.879 | 0.090975 | 708.345 | 0.07071 | 522.66 | 0.16478 | 999.176 | 0.10196 | 1585.93 | 0.074933 | 1263.86 | 0.13805 | 1027.54 | 0.31564 | 752.146 | 1.0973 | 1019.36 | 0.97126 | 1355.5 | 0.82188 | 1087.82 | 1.6158 | 1359.57 | 1.4548
799.456 | 0.040108 | 464.951 | 0.10602 | 630.764 | 0.083562 | 458.028 | 0.20677 | 912.265 | 0.11787 | 1416.48 | 0.088198 | 1126.56 | 0.16811 | 917.755 | 0.39056 | 683.982 | 1.3376 | 936.295 | 1.178 | 1257.56 | 0.9616 | 1015.29 | 1.9248 | 1271.47 | 1.7209
755.161 | 0.042504 | 419.025 | 0.12404 | 565.625 | 0.098651 | 399.387 | 0.26549 | 808.298 | 0.14469 | 1274.01 | 0.10381 | 1034.76 | 0.19453 | 842.97 | 0.45971 | 624.487 | 1.6255 | 848.043 | 1.4871 | 1165.52 | 1.1251 | 951.396 | 2.277 | 1205.83 | 1.9834
709.763 | 0.045087 | 382.96 | 0.14296 | 501.664 | 0.11846 | 356.356 | 0.32786 | 701.998 | 0.18486 | 1147.02 | 0.12256 | 883.535 | 0.2579 | 735.044 | 0.60341 | 575.323 | 1.952 | 777.381 | 1.8273 | 1084.56 | 1.319 | 904.996 | 2.6113 | 1145.88 | 2.2701
665.096 | 0.048598 | 352.458 | 0.1633 | 437.436 | 0.14791 | 301.85 | 0.45241 | 605.425 | 0.24192 | 1054.61 | 0.14112 | 797.858 | 0.31344 | 657.82 | 0.75793 | 526.331 | 2.3937 | 719.769 | 2.2341 | 1016.3 | 1.5248 | 861.72 | 3.0037 | 1084.56 | 2.6428
617.038 | 0.053016 | 323.737 | 0.18784 | 386.422 | 0.18084 | 269.328 | 0.56093 | 567.324 | 0.27413 | 958.08 | 0.16743 | 714.034 | 0.38668 | 567.892 | 1.0241 | 491.239 | 2.8515 | 675.823 | 2.6694 | 957.122 | 1.7521 | 819.694 | 3.5108 | 1032.69 | 3.046
559.437 | 0.059715 | 284.272 | 0.23547 | 330.277 | 0.23831 | 240.551 | 0.70246 | 515.394 | 0.32819 | 884.419 | 0.19337 | 655.849 | 0.45787 | 501.664 | 1.3269 | 464.486 | 3.2441 | 646.731 | 3.0613 | 898.683 | 2.048 | 786.766 | 4.0062 | 983.316 | 3.5496
514.364 | 0.066926 | 250.118 | 0.29459 | 288.28 | 0.30723 | 218.75 | 0.85713 | 469.154 | 0.39567 | 793.085 | 0.23736 | 606.031 | 0.54055 | 452.565 | 1.6734 | 442.275 | 3.6541 | 619.511 | 3.5284 | 844.657 | 2.3961 | 755.161 | 4.6036 | 938.17 | 4.1489
458.028 | 0.078539 | 219.408 | 0.37413 | 262.154 | 0.36745 | 194.402 | 1.1006 | 425.784 | 0.47895 | 712.608 | 0.28703 | 558.319 | 0.64329 | 409.088 | 2.1167 | 423.66 | 4.079 | 597.008 | 4.0505 | 807.49 | 2.726 | 729.917 | 5.2796 | 897.785 | 4.8059
408.679 | 0.092443 | 198.131 | 0.45332 | 234.611 | 0.45833 | 173.804 | 1.3991 | 384.495 | 0.58033 | 648.674 | 0.34022 | 504.683 | 0.7952 | 372.759 | 2.6774 | 406.641 | 4.5761 | 574.748 | 4.6267 | 773.504 | 3.1045 | 701.297 | 6.1463 | 861.72 | 5.5171
363.192 | 0.11045 | 185.848 | 0.51368 | 209.125 | 0.56941 | 156.324 | 1.7609 | 344.1 | 0.72458 | 578.207 | 0.42394 | 458.028 | 0.982 | 350.349 | 3.1107 | 388.748 | 5.2427 | 553.317 | 5.4132 | 737.253 | 3.5674 | 678.532 | 7.1267 | 835.417 | 6.2392
327.318 | 0.13027 | 174.676 | 0.58382 | 187.904 | 0.69966 | 144.739 | 2.0977 | 305.189 | 0.92112 | 523.706 | 0.51214 | 427.918 | 1.1432 | 331.601 | 3.6177 | 373.505 | 5.9053 | 532.153 | 6.3971 | 705.517 | 4.0708 | 657.162 | 8.2552 | 804.267 | 7.2634
290.886 | 0.15721 | 161.246 | 0.68581 | 168.499 | 0.86835 | 137.405 | 2.3651 | 272.035 | 1.1582 | 451.661 | 0.67627 | 393.835 | 1.37 | 318.917 | 4.0627 | 356 | 6.8063 | 516.942 | 7.2199 | 675.823 | 4.7154 | 637.103 | 9.5816 | 780.497 | 8.247
265.584 | 0.18375 | 148.998 | 0.80722 | 153.382 | 1.0532 | 130.965 | 2.6561 | 248.87 | 1.3769 | 402.595 | 0.84691 | 368.681 | 1.5934 | 307.026 | 4.5669 | 339.655 | 7.9394 | 503.675 | 8.2305 | 650.623 | 5.4241 | 620.752 | 10.9227 | 760.466 | 9.3637
237.681 | 0.22287 | 137.267 | 0.95108 | 144.45 | 1.1887 | 125.578 | 2.9442 | 224.288 | 1.7226 | 365.012 | 1.0231 | 333.596 | 2.0276 | 295.282 | 5.1492 | 326.664 | 9.2059 | 490.258 | 9.3264 | 630.764 | 6.1463 | 607.852 | 12.4391 | 743.175 | 10.5154
211.015 | 0.27716 | 127.094 | 1.1183 | 136.31 | 1.3591 | 120.293 | 3.2604 | 202.134 | 2.1573 | 328.63 | 1.2647 | 307.948 | 2.4445 | 286.555 | 5.7307 | 315.113 | 10.7064 | 480.07 | 10.442 | 610.288 | 7.0487 | 595.816 | 14.1518 | 724.826 | 12.2172
190.744 | 0.33448 | 116.971 | 1.3362 | 129.015 | 1.5278 | 114.655 | 3.6945 | 188.657 | 2.5316 | 299.146 | 1.5278 | 290.015 | 2.8316 | 275.319 | 6.6051 | 306.719 | 12.2294 | 468.217 | 11.8917 | 595.22 | 7.9394 | 581.105 | 16.7742 | 706.223 | 14.3227
170.022 | 0.41555 | 107.762 | 1.5918 | 122.6 | 1.7226 | 109.391 | 4.2242 | 178.026 | 2.9062 | 267.985 | 1.921 | 274.769 | 3.2604 | 263.468 | 7.8448 | 298.548 | 14.1094 | 457.113 | 13.6241 | 577.629 | 9.0779 | 569.598 | 19.6258 | 692.931 | 16.7742
150.044 | 0.53038 | 100.779 | 1.8383 | 116.388 | 1.9442 | 104.997 | 4.7343 | 169.513 | 3.2833 | 249.618 | 2.2431 | 261.892 | 3.7204 | 256.963 | 8.8184 | 291.468 | 15.9242 | 444.936 | 16.0843 | 566.191 | 10.2763 | 558.878 | 22.8247 | 677.853 | 19.8627
133.744 | 0.6609 | 93.6846 | 2.153 | 110.27 | 2.1833 | 100.88 | 5.338 | 162.541 | 3.6834 | 235.552 | 2.5698 | 251.12 | 4.22 | 248.621 | 10.2558 | 283.704 | 18.781 | 437.436 | 18.2259 | 553.871 | 11.4598 | 551.108 | 26.1761 | 661.779 | 23.8276
116.155 | 0.86488 | 89.0265 | 2.4372 | 103.952 | 2.4814 | 97.5079 | 5.9765 | 156.012 | 4.1572 | 225.638 | 2.8601 | 241.032 | 4.7819 | 241.756 | 11.8561 | 277.808 | 21.5817 | 428.775 | 20.7977 | 542.903 | 12.7795 | 542.903 | 30.1398 | 646.085 | 28.1303
103.744 | 1.081 | 85.1942 | 2.7315 | 98.6851 | 2.8118 | 93.8721 | 6.7318 | 149.744 | 4.6685 | 214.633 | 3.2474 | 232.742 | 5.3273 | 236.023 | 13.3277 | 272.035 | 24.9493 | 423.237 | 23.5905 | 531.09 | 14.3801 | 533.218 | 37.1085 | 630.764 | 34.1187
91.4629 | 1.3935 | 80.7158 | 3.1294 | 95.1004 | 3.0952 | 90.9158 | 7.5977 | 142.015 | 5.3862 | 205.394 | 3.6541 | 221.834 | 6.2267 | 231.35 | 14.9819 | 267.182 | 28.4414 | 416.519 | 26.7851 | 522.66 | 16.0361 | 524.23 | 45.0083 | 617.038 | 42.218
81.2827 | 1.7697 | 77.0099 | 3.5567 | 89.2939 | 3.6541 | 88.3171 | 8.5493 | 136.31 | 6.0427 | 196.749 | 4.1158 | 213.776 | 7.1624 | 226.996 | 16.9937 | 262.154 | 33.0773 | 409.498 | 31.0887 | 511.287 | 18.2624 | 516.942 | 53.5624 | 606.031 | 52.1878
72.8159 | 2.2319 | 73.2541 | 4.079 | 85.024 | 4.1906 | 86.6549 | 9.3919 | 130.182 | 6.9716 | 190.553 | 4.5533 | 207.044 | 8.1323 | 222.723 | 19.4111 | 257.735 | 38.739 | 402.998 | 35.9758 | 503.675 | 20.4063 | 510.265 | 64.2543 | 596.412 | 67.5487
65.1657 | 2.8658 | 69.9607 | 4.6592 | 81.0393 | 4.7581 | 85.024 | 10.547 | 124.952 | 8.0675 | 184.921 | 4.9523 | 201.126 | 9.1875 | 217.877 | 22.9162 | 252.127 | 47.4581 | 397.793 | 41.2581 | 494.69 | 23.1465 | 502.669 | 77.8551 | 584.602 | 86.7343
57.7968 | 3.8261 | 67.1503 | 5.248 | 77.7061 | 5.4024 | 83.4238 | 11.8561 | 120.654 | 9.1967 | 179.277 | 5.4403 | 195.572 | 10.4525 | 214.633 | 26.3599 | 247.381 | 59.7308 | 390.306 | 49.2962 | 487.325 | 26.4127 | 495.68 | 96.3367 | 573.026 | 117.196
53.2999 | 4.7154 | 63.8115 | 6.1095 | 74.0643 | 6.3208 | 82.0176 | 13.2347 | 117.44 | 10.5154 | 173.631 | 5.9945 | 191.126 | 11.703 | 211.015 | 30.4427 | 242.725 | 75.1773 | 382.577 | 60.2708 | 479.59 | 30.5036 | 490.258 | 120.043 | 561.679 | 164.325
49.8458 | 5.6624 | 61.3708 | 6.9646 | 71.5885 | 7.1839 | 80.3132 | 15.3458 | 114.885 | 11.7147 | 168.499 | 6.6515 | 187.154 | 13.2877 | 207.666 | 35.5822 | 236.969 | 99.868 | 377.259 | 73.615 | 471.977 | 35.6891 | 481.031 | 166.976 | 552.211 | 224.719
47.32 | 6.5525 | 58.6703 | 8.0756 | 69.1262 | 8.1812 | 78.9594 | 17.7049 | 111.936 | 13.3277 | 163.683 | 7.4398 | 181.986 | 15.5622 | 203.758 | 42.6423 | 231.35 | 135.077 | 370.9 | 89.734 | 464.486 | 42.5997 | 473.395 | 235.297 | 542.903 | 341.331
44.9672 | 7.6587 | 56.201 | 9.4107 | 66.8823 | 9.3919 | 77.9396 | 20.3248 | 109.83 | 15.1476 | 157.108 | 8.7045 | 176.784 | 18.4091 | 201.126 | 51.4622 | 226.316 | 186.205 | 363.192 | 119.086 | 455.288 | 52.9765 | 468.685 | 335.242 | 539.656 | 467.712
42.9456 | 8.7832 | 54.3766 | 10.547 | 64.4528 | 11.0324 | 76.4727 | 24.019 | 107.332 | 17.3544 | 152.312 | 9.7849 | 173.457 | 21.8422 | 197.341 | 63.361 | 221.391 | 257.714 | 354.934 | 160.75 | 448.959 | 63.9978 | 466.814 | 443.125 | 538.039 | 562.76
41.51 | 9.9527 | 52.981 | 11.9752 | 62.3606 | 12.8693 | 75.3342 | 28.2995 | 105.418 | 20.4267 | 148.998 | 11.0104 | 170.363 | 25.9156 | 193.82 | 81.1946 | 218.75 | 355.616 | 349.649 | 212.693 | 441.833 | 77.5443 | 465.416 | 570.694 | 536.427 | 602.961
40.4042 | 11.1545 | 51.4666 | 13.7336 | 60.9427 | 14.8625 | 73.9903 | 34.2212 | 103.021 | 23.8753 | 145.174 | 12.3399 | 167.659 | 30.5953 | 189.982 | 102.498 | 216.357 | 500.623 | 343.412 | 284.249 | 435.69 | 94.3347 | 464.951 | 606.59
39.525 | 12.665 | 50.2462 | 16.3274 | 59.8555 | 16.724 | 72.9616 | 40.0788 | 100.981 | 27.934 | 142.157 | 14.025 | 165.493 | 36.0478 | 186.034 | 135.077 | 215.278 | 607.805 | 337.961 | 385.234 | 429.633 | 114.875
38.5877 | 14.3083 | 49.0056 | 18.7434 | 59.0234 | 18.8751 | 72.0913 | 49.4443 | 98.8826 | 34.1529 | 139.203 | 15.75 | 163.029 | 43.5038 | 183.265 | 176.064 |  |  | 334.264 | 498.126 | 423.237 | 139.609
37.8994 | 16.5741 | 48.276 | 21.3456 | 58.2028 | 21.6682 | 71.0891 | 61.0595 | 97.3131 | 40.6032 | 136.037 | 18.2441 | 160.602 | 53.0295 | 181.079 | 239.571 |  |  | 331.269 | 607.805 | 416.519 | 181.789
36.8529 | 20.4063 | 47.6048 | 24.9742 | 57.5086 | 24.3576 | 70.1709 | 75.7054 | 95.9602 | 47.696 | 133.477 | 20.8602 | 157.895 | 64.641 | 179.456 | 309.777 |  |  |  |  | 409.907 | 237.187
35.979 | 24.9742 | 46.99 | 29.016 | 56.9933 | 27.7947 | 68.9191 | 98.0865 | 94.7208 | 56.365 | 131.227 | 23.4025 | 154.151 | 85.8713 | 178.383 | 402.161 |  |  |  |  | 405.018 | 301.826
35.2665 | 31.0887 | 46.2441 | 34.5997 | 56.201 | 33.1766 | 67.7574 | 137.944 | 93.4974 | 68.4326 | 130.051 | 26.7049 | 151.249 | 117.313 | 177.315 | 535.849 |  |  |  |  | 399.787 | 415.654
34.4991 | 41.0113 | 45.6468 | 40.5221 | 55.5861 | 41.6727 | 66.8823 | 193.224 | 92.5671 | 82.8349 | 128.757 | 29.9895 | 148.849 | 159.948 | 176.255 | 604.169 |  |  |  |  | 397.793 | 538.535
34.0535 | 54.4808 | 45.2378 | 48.7569 | 55.1432 | 51.9794 | 66.4822 | 249.598 | 91.8295 | 99.0723 | 126.587 | 35.4756 | 147.22 | 213.119 | [6 empty] | 395.809 | 606.59
33.8498 | 73.8362 | 44.8774 | 59.0183 | 54.978 | 80.3867 | 66.4157 | 605.378 | 91.2802 | 121.37 | 124.702 | 42.218 | 146.047 | 289.701
33.7147 | 101.478 | 44.5643 | 70.4462 | 54.8134 | 132.006 |  |  | 90.1914 | 158.04 | 123.092 | 49.4938 | 144.884 | 387.94
33.681 | 134.807 | 44.3864 | 83.2501 | 54.6492 | 246.128 |  |  | 89.1155 | 199.308 | 121.017 | 59.7906 | 144.305 | 512.271
33.6137 | 177.834 | 44.0768 | 101.276 | 54.5945 | 323.387 |  |  | 88.6711 | 263.447 | 119.693 | 69.8848 | 144.017 | 604.169
33.5466 | 248.105 | 43.9009 | 126.83 | 54.5945 | 609.021 |  |  | 88.4055 | 348.226 | 118.147 | 82.7521
33.5466 | 437.402 | 43.9009 | 208.481 |  |  |  |  | 88.4055 | 463.985 | 116.855 | 102.498
33.4126 | 531.58 | 43.857 | 349.622 |  |  |  |  | 88.3171 | 561.074 | 115.461 | 131.216
33.3792 | 602.961 | 43.8132 | 465.379 |  |  |  |  | 88.3171 | 607.197 | 113.288 | 175.712
|  | 44.7877 | 606.59 | [6 empty] | 112.385 | 223.822
[10 empty] | 111.824 | 292.906
[10 empty] | 111.044 | 411.518
[10 empty] | 110.712 | 605.984