## 119_2
S&C Power Fuses - Types SMU-20 and SMU-40 | [9 empty] | S&C Power Fuses - Types SMU-20 and SMU-40 | [9 empty] | S&C Power Fuses - Types SMU-20 and SMU-40 | [9 empty] | S&C Power Fuses - Types SMU-20 and SMU-40
Slow Speed (TCC 119-2) | [9 empty] | Slow Speed (TCC 119-2) | [9 empty] | Slow Speed (TCC 119-2) | [9 empty] | Slow Speed (TCC 119-2)
Minimum Melting Time-Current Characteristic Curves Dated June 17, 1991 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated June 17, 1991 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated June 17, 1991 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated June 17, 1991
Tolerance in Terms of Current: Plus 10% | [9 empty] | Tolerance in Terms of Current: Plus 10% | [9 empty] | Tolerance in Terms of Current: Plus 10% | [9 empty] | Tolerance in Terms of Current: Plus 10%
15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E |  | 250E |  | 300E |  | 400E |  | 2-250E |  | 2-300E |  | 2-400E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
930.694 | 0.01 | 1178.42 | 0.01 | 1359.57 | 0.01 | 1782.78 | 0.01 | 2596.52 | 0.01 | 3284.36 | 0.01 | 3943.91 | 0.01 | 5213.09 | 0.01 | 6713.85 | 0.01 | 8638.01 | 0.01 | 10806.7 | 0.01 | 11660.1 | 0.01 | 13628.6 | 0.01 | 16982.3 | 0.01 | 20372.2 | 0.01 | 26054 | 0.01 | 29999.2 | 0.010377 | 29999.2 | 0.014978 | 29999.2 | 0.024303
881.77 | 0.011107 | 1122.07 | 0.01103 | 1324.68 | 0.010555 | 1747.48 | 0.010419 | 2527.35 | 0.010555 | 3212.9 | 0.010429 | 3877.43 | 0.010377 | 5023.73 | 0.010714 | 6607.29 | 0.010356 | 8332.58 | 0.010704 | 10613.9 | 0.010398 | 11452 | 0.010408 | 13345.4 | 0.010419 | 15676.6 | 0.011712 | 19710.9 | 0.010704 | 24074.9 | 0.011723 | 28223.9 | 0.0117 | 29582.1 | 0.015403 | 28967.4 | 0.026013
805.877 | 0.013311 | 1040.99 | 0.012815 | 1250.04 | 0.011829 | 1677.28 | 0.01132 | 2413.73 | 0.011549 | 3111.71 | 0.011107 | 3740.33 | 0.011174 | 4807.48 | 0.011794 | 6348.21 | 0.01123 | 7942.06 | 0.011818 | 10269.4 | 0.011041 | 11058.2 | 0.01114 | 12938 | 0.011074 | 14284.4 | 0.014049 | 18268.3 | 0.012461 | 22046.9 | 0.013951 | 25717.5 | 0.013993 | 25258.7 | 0.021107 | 26027.9 | 0.032414
746.153 | 0.015481 | 964.81 | 0.014918 | 1177.24 | 0.013364 | 1603.47 | 0.012386 | 2286.84 | 0.01284 | 2965.88 | 0.012214 | 3597.26 | 0.012068 | 4582.17 | 0.01293 | 6038.6 | 0.012374 | 7494.53 | 0.013284 | 9946.02 | 0.011818 | 10645.8 | 0.012044 | 12543.1 | 0.011782 | 13146.7 | 0.016537 | 16431 | 0.015388 | 20028.8 | 0.016888 | 23669.1 | 0.016504 | 20762.9 | 0.031487 | 23504 | 0.039709
696.405 | 0.017789 | 887.076 | 0.017665 | 1083.47 | 0.015762 | 1517.66 | 0.013854 | 2162.3 | 0.014333 | 2795.95 | 0.013744 | 3401.35 | 0.013485 | 4354.34 | 0.01429 | 5761.36 | 0.013634 | 7065.14 | 0.014918 | 9556.03 | 0.012789 | 10248.9 | 0.012982 | 12123.8 | 0.012611 | 11883.7 | 0.020279 | 14029.6 | 0.021149 | 18014.4 | 0.020855 | 21395.3 | 0.020299 | 18323.2 | 0.040189 | 20950.7 | 0.050279
637.74 | 0.021212 | 806.683 | 0.021361 | 1001.17 | 0.018478 | 1419.31 | 0.015793 | 2024.2 | 0.016389 | 2648.98 | 0.015327 | 3222.55 | 0.015023 | 4092.57 | 0.016193 | 5318.4 | 0.016 | 6633.77 | 0.016888 | 8945.7 | 0.014564 | 9866.77 | 0.014021 | 11578.7 | 0.013854 | 10959.1 | 0.023845 | 11532.5 | 0.031456 | 16089.5 | 0.026039 | 19730.6 | 0.023893 | 15582.8 | 0.055678 | 19109.2 | 0.060075
577.051 | 0.025857 | 734.31 | 0.02578 | 886.19 | 0.023679 | 1322.03 | 0.018276 | 1883.58 | 0.018908 | 2489.73 | 0.01735 | 3056.2 | 0.01672 | 3858.09 | 0.018331 | 4998.68 | 0.018167 | 6234.96 | 0.019155 | 8492.41 | 0.016209 | 9470.41 | 0.01522 | 11080.3 | 0.015174 | 10136.8 | 0.027815 | 10177.4 | 0.040189 | 14456.9 | 0.032382 | 18250.1 | 0.027788 | 13959.6 | 0.069518 | 17534.5 | 0.071707
521.094 | 0.031772 | 677.176 | 0.030313 | 776.604 | 0.030618 | 1227.74 | 0.021255 | 1768.57 | 0.021511 | 2335.38 | 0.019719 | 2886.87 | 0.018739 | 3622.53 | 0.020709 | 4702.87 | 0.020462 | 5819.26 | 0.022056 | 8021.88 | 0.018185 | 9144.68 | 0.016356 | 10613.9 | 0.016537 | 9320.09 | 0.032904 | 8655.31 | 0.055678 | 13055 | 0.039749 | 16779.7 | 0.032904 | 11578.7 | 0.10034 | 16089.5 | 0.08491
463.558 | 0.039948 | 623.863 | 0.035751 | 692.931 | 0.038652 | 1152.77 | 0.024206 | 1650.66 | 0.024695 | 2186.22 | 0.022547 | 2737.85 | 0.020855 | 3374.25 | 0.023941 | 4393.71 | 0.023514 | 5431.27 | 0.025244 | 7554.72 | 0.020442 | 8768.56 | 0.017754 | 10136.8 | 0.018167 | 8733.56 | 0.037397 | 7753.72 | 0.069518 | 11636.8 | 0.050279 | 15723.7 | 0.037397 | 10116.5 | 0.13131 | 14912 | 0.099245
415.686 | 0.049729 | 579.944 | 0.04133 | 630.133 | 0.046693 | 1064.14 | 0.028377 | 1535.99 | 0.028434 | 2038.42 | 0.025909 | 2552.75 | 0.023893 | 3155.58 | 0.027346 | 4141.98 | 0.026432 | 5114.98 | 0.028491 | 7222.3 | 0.022367 | 8365.97 | 0.019464 | 9623.16 | 0.020057 | 7942.06 | 0.045358 | 6431.28 | 0.10034 | 10613.9 | 0.060135 | 14298.7 | 0.045403 | 9236.59 | 0.1569 | 13724.3 | 0.11693
375.002 | 0.060983 | 533.218 | 0.048891 | 568.46 | 0.057431 | 987.257 | 0.032937 | 1416.48 | 0.033368 | 1910.13 | 0.029506 | 2399.29 | 0.027129 | 2942.25 | 0.031487 | 3774.14 | 0.031868 | 4802.67 | 0.032446 | 6727.29 | 0.025883 | 7878.78 | 0.022078 | 9089.98 | 0.022569 | 7086.37 | 0.056803 | 5619.11 | 0.13131 | 9739.33 | 0.071707 | 12758.1 | 0.056803 | 8492.41 | 0.18634 | 12480.5 | 0.14083
329.287 | 0.078932 | 487.325 | 0.058709 | 510.265 | 0.071207 | 894.201 | 0.040108 | 1303.65 | 0.039236 | 1761.51 | 0.03466 | 2192.79 | 0.032446 | 2702.49 | 0.037248 | 3483.97 | 0.037434 | 4336.96 | 0.03959 | 6148.28 | 0.030926 | 7494.53 | 0.0244 | 8534.98 | 0.025651 | 6489.42 | 0.067734 | 5130.35 | 0.1569 | 8936.76 | 0.08491 | 11683.4 | 0.067734 | 7761.48 | 0.22354 | 11180.5 | 0.17497
300.345 | 0.094878 | 451.661 | 0.06821 | 461.707 | 0.087146 | 811.538 | 0.048891 | 1197.42 | 0.046506 | 1624.45 | 0.040837 | 2018.13 | 0.038305 | 2494.71 | 0.043754 | 3258.19 | 0.042802 | 3999.51 | 0.046413 | 5732.62 | 0.035573 | 7114.77 | 0.027047 | 8045.98 | 0.028864 | 6099.29 | 0.076983 | 4717 | 0.18634 | 8282.73 | 0.099245 | 10981 | 0.076983 | 6876.93 | 0.28503 | 10320.9 | 0.20553
266.648 | 0.12049 | 415.271 | 0.080446 | 431.355 | 0.099842 | 721.932 | 0.061472 | 1099.85 | 0.054959 | 1511.61 | 0.047256 | 1887.35 | 0.04393 | 2316.77 | 0.050632 | 3013.71 | 0.050028 | 3662.6 | 0.055456 | 5377.23 | 0.040471 | 6767.78 | 0.029892 | 7607.79 | 0.032446 | 5681.26 | 0.088463 | 4311.01 | 0.22354 | 7623.02 | 0.11693 | 10228.4 | 0.088463 | 6203.87 | 0.35058 | 9489.37 | 0.24362
230.888 | 0.16007 | 379.15 | 0.096794 | 400.988 | 0.11542 | 665.096 | 0.072718 | 1027.54 | 0.062966 | 1417.89 | 0.053709 | 1726.63 | 0.052331 | 2115.25 | 0.060678 | 2818.41 | 0.057374 | 3377.63 | 0.065143 | 5094.56 | 0.045087 | 6329.19 | 0.034212 | 7236.75 | 0.035895 | 5207.88 | 0.10517 | 3819.7 | 0.28503 | 6932.17 | 0.14083 | 9376.18 | 0.10517 | 5469.42 | 0.45016 | 8892.18 | 0.27883
201.528 | 0.21052 | 345.479 | 0.11693 | 363.919 | 0.13985 | 612.734 | 0.086193 | 944.76 | 0.074559 | 1324.68 | 0.061411 | 1578.02 | 0.062714 | 1929.33 | 0.072718 | 2617.38 | 0.066393 | 3090.01 | 0.077835 | 4807.48 | 0.050481 | 5936.82 | 0.038962 | 6835.8 | 0.04031 | 4846.09 | 0.12134 | 3445.86 | 0.35058 | 6210.07 | 0.17497 | 8724.83 | 0.12134 | 4899.69 | 0.56205 | 8094.4 | 0.33852
181.804 | 0.2579 | 313.855 | 0.14055 | 330.938 | 0.16878 | 559.997 | 0.10268 | 880.008 | 0.085849 | 1236.36 | 0.070287 | 1453.79 | 0.073743 | 1766.8 | 0.087059 | 2333.04 | 0.083562 | 2821.23 | 0.093092 | 4500.43 | 0.057661 | 5613.49 | 0.043711 | 6521.95 | 0.044327 | 4406.91 | 0.14629 | 3037.92 | 0.45016 | 5732.62 | 0.20553 | 7934.12 | 0.14629 | 4415.73 | 0.70528 | 7368.2 | 0.41513
162.379 | 0.3246 | 287.416 | 0.16794 | 303.971 | 0.20006 | 504.683 | 0.12629 | 819.694 | 0.098849 | 1142.45 | 0.081907 | 1333.99 | 0.087408 | 1613.12 | 0.10433 | 2149.37 | 0.098454 | 2601.72 | 0.10957 | 4272.39 | 0.063917 | 5207.88 | 0.050683 | 6087.11 | 0.050784 | 4113.08 | 0.16777 | 2721.47 | 0.56205 | 5270.75 | 0.24362 | 7405.13 | 0.16777 | 3947.86 | 0.9065 | 6515.43 | 0.54164
148.254 | 0.38862 | 264.524 | 0.19787 | 277.808 | 0.23927 | 460.785 | 0.1515 | 762.75 | 0.11393 | 1056.72 | 0.096312 | 1258.82 | 0.098553 | 1480.19 | 0.12305 | 1966.34 | 0.11764 | 2413.73 | 0.12731 | 4039.71 | 0.071421 | 4885.02 | 0.057777 | 5761.36 | 0.05686 | 3812.07 | 0.19492 | 2452.66 | 0.70528 | 4939.05 | 0.27883 | 6863.19 | 0.19492 | 3533.09 | 1.1768 | 5732.62 | 0.73406
136.583 | 0.45787 | 242.24 | 0.23665 | 255.426 | 0.28389 | 409.498 | 0.19106 | 702.701 | 0.1337 | 982.333 | 0.11101 | 1179.6 | 0.11201 | 1367.76 | 0.14411 | 1807.91 | 0.13902 | 2248.3 | 0.14629 | 3854.24 | 0.078617 | 4665.4 | 0.063155 | 5425.84 | 0.063981 | 3557.91 | 0.22421 | 2192.79 | 0.9065 | 4495.93 | 0.33852 | 6405.6 | 0.22421 | 3248.43 | 1.4621 | 5239.22 | 0.91836
127.094 | 0.53091 | 224.962 | 0.27385 | 235.081 | 0.33382 | 369.419 | 0.235 | 656.505 | 0.15364 | 916.838 | 0.12794 | 1108.68 | 0.12705 | 1265.13 | 0.16743 | 1660.59 | 0.16428 | 2113.14 | 0.16544 | 3673.6 | 0.086452 | 4358.7 | 0.072355 | 5109.86 | 0.072139 | 3245.19 | 0.26897 | 1962.41 | 1.1768 | 4092.57 | 0.41513 | 5842.58 | 0.26897 | 2956.99 | 1.8717 | 4802.67 | 1.1421
110.27 | 0.70528 | 206.424 | 0.3246 | 217.224 | 0.39135 | 345.133 | 0.27005 | 607.852 | 0.17958 | 842.97 | 0.1509 | 1040.99 | 0.14397 | 1163.2 | 0.19826 | 1560.76 | 0.18597 | 1970.27 | 0.19068 | 3487.46 | 0.095353 | 4154.42 | 0.079805 | 4817.1 | 0.08085 | 2968.84 | 0.32169 | 1804.3 | 1.4621 | 3618.91 | 0.54164 | 5345.06 | 0.32169 | 2729.65 | 2.3393 | 4411.32 | 1.426
98.0947 | 0.8948 | 188.846 | 0.38706 | 203.961 | 0.44479 | 309.492 | 0.33515 | 566.757 | 0.20615 | 743.175 | 0.19356 | 971.587 | 0.16511 | 1072.69 | 0.23243 | 1426.43 | 0.2222 | 1853.68 | 0.21628 | 3290.94 | 0.1073 | 3912.49 | 0.08989 | 4618.98 | 0.08811 | 2759.84 | 0.37189 | 1642.42 | 1.8717 | 3184.11 | 0.73406 | 4968.77 | 0.37189 | 2547.65 | 2.883 | 4113.08 | 1.7382
88.6711 | 1.0984 | 172.075 | 0.46479 | 191.508 | 0.5025 | 281.162 | 0.40691 | 523.706 | 0.24071 | 668.43 | 0.23951 | 895.096 | 0.19473 | 995.187 | 0.26897 | 1344.7 | 0.25003 | 1721.46 | 0.24953 | 3114.82 | 0.11977 | 3762.84 | 0.09728 | 4420.15 | 0.096312 | 2593.93 | 0.42267 | 1516.15 | 2.3393 | 2910.06 | 0.91836 | 4670.06 | 0.42267 | 2392.1 | 3.5781 | 3800.65 | 2.2207
81.2015 | 1.3256 | 150.796 | 0.61314 | 179.098 | 0.57169 | 262.154 | 0.46853 | 492.223 | 0.27249 | 607.852 | 0.28847 | 840.444 | 0.22087 | 928.835 | 0.30815 | 1275.29 | 0.27911 | 1613.12 | 0.28531 | 2933.43 | 0.13491 | 3593.67 | 0.10644 | 4238.35 | 0.10475 | 2418.56 | 0.49009 | 1415.06 | 2.883 | 2667.58 | 1.1421 | 4354.34 | 0.49009 | 2243.8 | 4.6406 | 3526.03 | 2.8543
73.9903 | 1.6094 | 134.953 | 0.76402 | 162.704 | 0.69408 | 245.901 | 0.52985 | 457.113 | 0.31564 | 550.557 | 0.35093 | 782.842 | 0.25483 | 866.04 | 0.35411 | 1185.51 | 0.32363 | 1510.09 | 0.3259 | 2795.95 | 0.1482 | 3425.24 | 0.11728 | 3896.87 | 0.12367 | 2223.7 | 0.58792 | 1328.66 | 3.5781 | 2450.21 | 1.426 | 4003.52 | 0.58792 | 2119.48 | 5.9467 | 3245.19 | 3.9269
68.37 | 1.9133 | 122.478 | 0.93131 | 151.401 | 0.80319 | 231.813 | 0.59264 | 423.66 | 0.36745 | 499.662 | 0.42735 | 730.647 | 0.29254 | 808.298 | 0.40569 | 1107.57 | 0.373 | 1410.82 | 0.3745 | 2659.59 | 0.16363 | 3206.48 | 0.13423 | 3729.12 | 0.13531 | 2052.73 | 0.69966 | 1246.29 | 4.6406 | 2284.56 | 1.7382 | 3695.71 | 0.69966 | 2036.38 | 7.1911 | 3031.85 | 5.6285
63.8754 | 2.2319 | 111.155 | 1.1421 | 141.731 | 0.92389 | 215.063 | 0.68649 | 391.087 | 0.43164 | 455.288 | 0.51419 | 681.933 | 0.3365 | 749.893 | 0.46853 | 1027.54 | 0.43598 | 1332.65 | 0.4214 | 2504.71 | 0.18449 | 3010.7 | 0.15226 | 3526.03 | 0.15014 | 1896.81 | 0.83681 | 1177.24 | 5.9467 | 2111.02 | 2.2207 | 3414.98 | 0.83681 | 1933.19 | 9.6296 | 2895.54 | 7.7589
60.276 | 2.5698 | 100.779 | 1.4132 | 132.281 | 1.0702 | 202.134 | 0.78102 | 362.104 | 0.502 | 418.606 | 0.60341 | 639.017 | 0.38321 | 696.405 | 0.54544 | 959.038 | 0.502 | 1257.56 | 0.47608 | 2351.78 | 0.20905 | 2852.43 | 0.16997 | 3337.34 | 0.1666 | 1772.11 | 0.98102 | 1131.08 | 7.1911 | 1958.49 | 2.8543 | 3190.49 | 0.98102 | 1861.11 | 12.464 | 2790.37 | 10.0527
56.7658 | 2.9679 | 90.9158 | 1.7804 | 121.989 | 1.2761 | 187.528 | 0.90923 | 334.933 | 0.58324 | 382.577 | 0.71809 | 582.268 | 0.4634 | 657.82 | 0.60886 | 881.77 | 0.598 | 1199.82 | 0.52353 | 2210.4 | 0.23665 | 2670.25 | 0.19356 | 3124.18 | 0.18992 | 1603.47 | 1.2496 | 1073.77 | 9.6296 | 1802.5 | 3.9269 | 2886.87 | 1.2496 | 1793.51 | 16.4915 | 2686.32 | 12.8821
53.7817 | 3.4002 | 85.024 | 2.0685 | 113.514 | 1.4916 | 176.784 | 1.0272 | 296.169 | 0.74814 | 352.458 | 0.84522 | 529.499 | 0.5643 | 614.575 | 0.69547 | 832.914 | 0.6783 | 1141.3 | 0.58499 | 2063.02 | 0.27194 | 2482.27 | 0.22421 | 2927.57 | 0.21628 | 1498.06 | 1.4916 | 1033.73 | 12.464 | 1684 | 5.6285 | 2697.09 | 1.4916 | 1749.22 | 21.6682 | 2588.74 | 17.1131
50.6497 | 3.9465 | 79.4346 | 2.4274 | 104.369 | 1.8091 | 166.489 | 1.1651 | 270.678 | 0.89569 | 329.287 | 0.96835 | 483.926 | 0.6817 | 566.191 | 0.82188 | 777.381 | 0.78729 | 1083.47 | 0.65301 | 1976.19 | 0.29518 | 2358.85 | 0.24829 | 2765.37 | 0.24289 | 1422.15 | 1.7226 | 996.183 | 16.4915 | 1608.29 | 7.7589 | 2560.42 | 1.7226 | 1704.33 | 27.5181 | 2492.22 | 23.426
47.4148 | 4.7296 | 74.7339 | 2.809 | 98.6851 | 2.0541 | 158.053 | 1.3045 | 247.629 | 1.0766 | 307.333 | 1.1161 | 452.565 | 0.78572 | 530.559 | 0.93318 | 730.647 | 0.90289 | 1035.8 | 0.71953 | 1831.57 | 0.34158 | 2205.98 | 0.28418 | 2622.62 | 0.27032 | 1359.57 | 1.9539 | 971.587 | 21.6682 | 1549.87 | 10.0527 | 2447.76 | 1.9539 | 1658.93 | 35.5822 | 2389.71 | 32.5848
44.6982 | 5.6116 | 70.2411 | 3.2734 | 93.7783 | 2.2929 | 149.296 | 1.4738 | 229.506 | 1.2596 | 285.983 | 1.2967 | 425.784 | 0.8939 | 501.163 | 1.05 | 676.499 | 1.0723 | 993.199 | 0.79044 | 1731.82 | 0.38207 | 2032.31 | 0.33448 | 2472.36 | 0.30478 | 1285.53 | 2.3114 | 946.651 | 27.5181 | 1492.08 | 12.8821 | 2314.45 | 2.3114 | 1626.08 | 45.8258 | 2314.45 | 41.7979
42.1795 | 6.6051 | 67.0832 | 3.6982 | 89.4727 | 2.5417 | 141.448 | 1.6617 | 213.99 | 1.4635 | 266.382 | 1.5096 | 398.191 | 1.0375 | 469.623 | 1.197 | 635.194 | 1.2273 | 940.988 | 0.89033 | 1640.78 | 0.42692 | 1900.61 | 0.38207 | 2330.71 | 0.3433 | 1198.62 | 2.8801 | 921.434 | 35.5822 | 1437.88 | 17.1131 | 2157.98 | 2.8801 | 1589.11 | 60.0302 | 2239.32 | 54.5898
40.1625 | 7.6894 | 63.3664 | 4.3225 | 84.8541 | 2.8917 | 134.549 | 1.8568 | 202.539 | 1.6534 | 251.12 | 1.7157 | 377.259 | 1.1686 | 446.72 | 1.3282 | 591.068 | 1.4331 | 899.583 | 0.98594 | 1552.97 | 0.47656 | 1795.3 | 0.42949 | 2205.98 | 0.38398 | 1142.45 | 3.4413 | 903.188 | 45.8258 | 1384.27 | 23.426 | 2056.84 | 3.4413 | 1554.53 | 78.402 | 2186.22 | 68.6382
38.3953 | 8.8008 | 60.0954 | 5.007 | 81.2015 | 3.2474 | 127.094 | 2.1209 | 190.363 | 1.8981 | 234.377 | 1.9994 | 359.219 | 1.3006 | 426.21 | 1.4708 | 554.979 | 1.6452 | 865.174 | 1.0777 | 1442.2 | 0.55368 | 1692.44 | 0.48328 | 2087.93 | 0.43164 | 1088.9 | 4.1282 | 882.652 | 60.0302 | 1327.33 | 32.5848 | 1960.45 | 4.1282 | 1523.75 | 101.681 | 2134.37 | 86.6476
36.9636 | 10.1334 | 56.8794 | 5.8817 | 77.3959 | 3.6871 | 120.413 | 2.4178 | 178.919 | 2.1746 | 220.949 | 2.2998 | 338.977 | 1.4871 | 404.209 | 1.6567 | 525.28 | 1.8605 | 822.157 | 1.2163 | 1355.5 | 0.62866 | 1621.21 | 0.52773 | 1970.27 | 0.48716 | 1042.03 | 4.9177 | 863.446 | 78.402 | 1285.53 | 41.7979 | 1876.06 | 4.9177 | 1495.07 | 126.576 | 2069.22 | 112.6
35.7637 | 11.703 | 54.1595 | 6.916 | 74.4356 | 4.1158 | 115.23 | 2.6989 | 166.489 | 2.5853 | 208.916 | 2.6244 | 323.09 | 1.6617 | 382.195 | 1.8886 | 501.664 | 2.0789 | 785.194 | 1.3564 | 1294.56 | 0.69131 | 1539.06 | 0.58792 | 1881.69 | 0.53625 | 1004.18 | 5.7999 | 846.348 | 101.681 | 1243.8 | 54.5898 | 1807.91 | 5.7999 | 1459.61 | 168.823 | 2024.2 | 137.393
34.3958 | 14.3083 | 51.7764 | 8.1242 | 71.3027 | 4.636 | 109.501 | 3.0736 | 158.528 | 2.9033 | 199.723 | 2.9442 | 304.884 | 1.9038 | 363.192 | 2.1358 | 479.59 | 2.2998 | 755.917 | 1.4856 | 1224.06 | 0.78258 | 1456.7 | 0.65826 | 1782.78 | 0.6004 | 969.646 | 6.8609 | 830.419 | 126.576 | 1214.3 | 68.6382 | 1745.73 | 6.8609 | 1426.43 | 218.077 | 1978.17 | 172.578
33.3459 | 17.5814 | 49.6468 | 9.5338 | 68.7127 | 5.2218 | 104.369 | 3.4863 | 149.445 | 3.3529 | 188.846 | 3.407 | 293.222 | 2.0893 | 347.21 | 2.3889 | 453.018 | 2.6402 | 727.731 | 1.6386 | 1162.03 | 0.87708 | 1395.39 | 0.72241 | 1684 | 0.67695 | 940.988 | 7.9793 | 810.727 | 168.823 | 1185.51 | 86.6476 | 1694.14 | 7.9793 | 1392.6 | 290.572 | 1940.94 | 205.994
32.4251 | 21.7333 | 47.8434 | 11.188 | 66.6819 | 5.8348 | 100.076 | 3.9073 | 141.024 | 3.9034 | 179.995 | 3.8568 | 282.007 | 2.2975 | 329.947 | 2.7097 | 428.346 | 3.0187 | 688.786 | 1.8886 | 1092.18 | 1.0008 | 1333.99 | 0.79441 | 1592.29 | 0.77016 | 905.902 | 9.7849 | 792.293 | 218.077 | 1149.32 | 112.6 | 1630.97 | 9.7849 | 1363.66 | 378.362 | 1896.81 | 253.877
31.8467 | 25.9156 | 46.2904 | 13.2479 | 64.1956 | 6.7927 | 95.6728 | 4.4497 | 135.494 | 4.3747 | 172.592 | 4.3486 | 273.125 | 2.5039 | 312.915 | 3.12 | 405.829 | 3.431 | 653.231 | 2.1746 | 1043.07 | 1.1094 | 1263.86 | 0.88944 | 1529.85 | 0.84016 | 874.744 | 12.1077 | 773.504 | 290.572 | 1124.31 | 137.393 | 1574.87 | 12.1077 | 1324.68 | 500.122 | 1851.83 | 315.719
31.2161 | 32.5522 | 45.1475 | 15.4536 | 61.9876 | 7.8605 | 92.0134 | 5.002 | 131.096 | 4.7963 | 166.656 | 4.83 | 261.368 | 2.7839 | 298.847 | 3.539 | 387.196 | 3.8878 | 625.738 | 2.4469 | 986.271 | 1.2609 | 1213.09 | 0.97613 | 1455.24 | 0.93879 | 844.657 | 15.4227 | 757.43 | 378.362 | 1098.75 | 172.578 | 1520.7 | 15.4227 | 1311.5 | 588.663 | 1806.1 | 398.558
30.7514 | 39.2459 | 43.9888 | 18.5384 | 59.7359 | 9.2613 | 88.5824 | 5.6173 | 126.082 | 5.3273 | 162.054 | 5.2743 | 253.39 | 3.0278 | 284.841 | 4.0505 | 372.014 | 4.3269 | 604.82 | 2.7097 | 942.872 | 1.3963 | 1163.2 | 1.0702 | 1393.99 | 1.0354 | 820.514 | 19.2179 | 735.78 | 500.122 | 1078.07 | 205.994 | 1477.24 | 19.2179 | 1306.26 | 604.773 | 1759.75 | 501.625
30.4149 | 48.3684 | 43.2473 | 21.5817 | 57.7968 | 10.8465 | 85.5357 | 6.3334 | 121.38 | 5.9171 | 156.012 | 5.9289 | 243.942 | 3.3529 | 272.035 | 4.6779 | 357.785 | 4.8396 | 584.018 | 3.0097 | 901.384 | 1.5525 | 1116.47 | 1.1804 | 1328.66 | 1.1616 | 791.501 | 25.8638 | 728.459 | 588.663 | 1053.56 | 253.877 | 1425 | 25.8638 |  |  | 1731.82 | 580.479
30.2028 | 60.0302 | 42.7314 | 25.2252 | 56.4262 | 12.3894 | 82.7591 | 7.1124 | 116.621 | 6.7251 | 150.947 | 6.6316 | 234.846 | 3.7279 | 261.892 | 5.2427 | 343.756 | 5.4349 | 563.367 | 3.3664 | 854.854 | 1.7697 | 1065.21 | 1.3111 | 1266.39 | 1.3006 | 774.278 | 32.0035 | 725.551 | 604.773 | 1028.57 | 315.719 | 1393.99 | 32.0035 |  |  | 1723.18 | 604.773
30.0822 | 78.9527 | 42.1373 | 29.6317 | 55.0881 | 14.3944 | 80.3132 | 8.0112 | 112.385 | 7.6741 | 147.073 | 7.3437 | 227.223 | 4.0994 | 253.137 | 5.8935 | 330.938 | 6.0548 | 541.277 | 3.8956 | 813.162 | 2.0014 | 1030.63 | 1.4132 | 1211.88 | 1.4504 | 750.644 | 41.2994 |  |  | 1003.18 | 398.558 | 1351.44 | 41.2994
30.0221 | 108.185 | 41.6764 | 34.669 | 54.0513 | 16.7407 | 78.0956 | 9.0961 | 108.954 | 8.6438 | 142.726 | 8.2966 | 218.969 | 4.599 | 243.455 | 6.7318 | 319.875 | 6.7116 | 526.331 | 4.3225 | 778.159 | 2.2431 | 993.199 | 1.5463 | 1160.87 | 1.6207 | 727.731 | 52.765 |  |  | 977.434 | 501.625 | 1310.19 | 52.765
29.9921 | 153.216 | 41.2204 | 40.8476 | 53.2466 | 19.3336 | 76.3199 | 10.3072 | 105.312 | 10.1436 | 138.093 | 9.4013 | 212.073 | 5.0827 | 236.023 | 7.6358 | 307.333 | 7.5825 | 509.755 | 4.8981 | 748.395 | 2.4914 | 956.165 | 1.6885 | 1109.79 | 1.8164 | 709.763 | 67.2118 |  |  | 961.92 | 580.479 | 1277.84 | 67.2118
29.9921 | 221.152 | 40.8511 | 48.4653 | 52.4539 | 23.1929 | 74.2126 | 12.0112 | 102.098 | 11.7852 | 134.415 | 10.7708 | 205.805 | 5.6116 | 228.59 | 8.8715 | 298.847 | 8.4304 | 495.68 | 5.484 | 721.21 | 2.7562 | 926.979 | 1.831 | 1070.55 | 2.0034 | 695.013 | 81.9287 |  |  | 957.122 | 604.773 | 1251.29 | 81.9287
30.0221 | 317.301 | 40.5256 | 58.6066 | 51.7764 | 27.5732 | 72.4527 | 13.9411 | 99.279 | 13.6105 | 130.834 | 12.3646 | 199.923 | 6.1771 | 222.056 | 10.1334 | 290.886 | 9.4013 | 479.11 | 6.3716 | 694.319 | 3.0828 | 885.304 | 2.0582 | 1024.47 | 2.2633 | 677.853 | 104.36 |  |  |  |  | 1220.39 | 104.36
29.9921 | 467.712 | 40.3638 | 72.4465 | 51.21 | 33.3096 | 70.8761 | 15.9721 | 96.8278 | 15.9402 | 127.859 | 14.166 | 193.046 | 7.0487 | 217.659 | 11.4026 | 285.126 | 10.2763 | 464.486 | 7.3437 | 668.43 | 3.4482 | 857.423 | 2.2386 | 980.371 | 2.5596 | 664.431 | 130.954 |  |  |  |  | 1196.23 | 130.954
29.9621 | 545.582 | 40.1625 | 91.5467 | 50.7004 | 40.0387 | 69.8908 | 18.0445 | 95.1004 | 18.2441 | 124.578 | 16.6739 | 186.22 | 8.0353 | 212.498 | 12.895 | 277.253 | 11.7499 | 453.018 | 8.3632 | 642.22 | 3.9034 | 827.104 | 2.4641 | 946.651 | 2.8231 | 649.323 | 167.981 |  |  |  |  | 1169.03 | 167.981
29.9322 | 601.155 | 40.0422 | 121.492 | 50.3467 | 49.2962 | 68.5754 | 21.2604 | 93.2173 | 21.3456 | 121.867 | 19.3529 | 180.536 | 9.16 | 208.916 | 14.4377 | 271.763 | 13.103 | 441.833 | 9.5912 | 620.752 | 4.3572 | 799.456 | 2.7315 | 911.353 | 3.1831 | 635.194 | 222.038 |  |  |  |  | 1143.59 | 222.038
|  | 40.0422 | 157.095 | 50.1959 | 62.4177 | 67.4195 | 24.7505 | 91.3715 | 25.0493 | 118.502 | 23.4729 | 174.85 | 10.5575 | 205.189 | 16.1488 | 265.584 | 14.7294 | 431.355 | 10.9336 | 600.001 | 4.9079 | 775.828 | 2.9738 | 882.652 | 3.5284 | 623.24 | 288.545 |  |  |  |  | 1122.07 | 288.545
|  | 40.0823 | 198.115 | 50.1959 | 81.8468 | 66.5487 | 28.987 | 89.6518 | 29.1031 | 116.388 | 27.7947 | 170.193 | 12.0594 | 201.73 | 18.1169 | 259.545 | 16.8078 | 422.391 | 12.3523 | 577.629 | 5.6511 | 752.899 | 3.2539 | 854.854 | 3.9308 | 612.122 | 367.915 |  |  |  |  | 1102.05 | 367.915
|  | 40.1224 | 273.924 | 50.1458 | 111.035 | 65.5579 | 34.3241 | 88.5824 | 33.5436 | 114.198 | 32.9452 | 165.659 | 14.294 | 196.946 | 21.2816 | 254.406 | 19.0077 | 411.55 | 14.6559 | 564.495 | 6.2205 | 730.647 | 3.5532 | 825.452 | 4.4453 | 603.612 | 462.595 |  |  |  |  | 1086.73 | 462.595
|  | 40.1625 | 357.041 | 50.1458 | 143.861 | 64.7112 | 41.2994 | 87.1764 | 39.839 | 112.497 | 38.7003 | 162.216 | 16.5576 | 193.82 | 24.7257 | 248.621 | 21.9737 | 402.193 | 17.2161 | 548.36 | 7.077 | 711.184 | 3.8607 | 802.66 | 4.9424 | 596.412 | 604.773 |  |  |  |  | 1073.77 | 604.773
|  | 40.0823 | 437.402 | 50.1959 | 187.889 | 64.0033 | 50.2418 | 86.0505 | 46.7516 | 111.044 | 45.5972 | 158.686 | 19.2179 | 190.363 | 29.425 | 242.483 | 26.0195 | 394.623 | 19.8032 | 534.82 | 7.9872 | 694.319 | 4.2116 | 776.604 | 5.6116
|  | 40.0422 | 541.776 | 50.1959 | 253.623 | 63.2398 | 61.2429 | 84.939 | 56.0278 | 109.501 | 55.4703 | 154.768 | 23.2161 | 186.407 | 36.12 | 238.395 | 29.6614 | 386.809 | 23.3324 | 521.094 | 9.087 | 675.823 | 4.6452 | 749.893 | 6.5328
|  | 40.0022 | 609.021 | 50.1959 | 345.451 | 62.7359 | 73.8362 | 84.2622 | 65.8809 | 108.303 | 65.6835 | 152.312 | 27.6561 | 182.898 | 43.9849 | 234.377 | 34.669 | 379.909 | 27.2716 | 510.776 | 10.2558 | 655.194 | 5.2166 | 730.647 | 7.3584
|  |  |  | 50.1959 | 466.777 | 62.1117 | 90.8173 | 83.5073 | 77.2347 | 106.904 | 81.765 | 149.744 | 33.1766 | 179.815 | 53.9926 | 230.657 | 39.2459 | 372.759 | 31.8121 | 498.165 | 11.703 | 639.656 | 5.7595 | 709.053 | 8.4388
|  |  |  | 50.1959 | 566.713 | 61.6784 | 113.618 | 82.8419 | 91.9136 | 105.629 | 103.115 | 147.663 | 39.9587 | 177.493 | 63.4244 | 227.223 | 45.3245 | 366.109 | 38.1241 | 486.351 | 13.5562 | 623.863 | 6.3907 | 688.786 | 9.9229
|  |  |  | 50.1458 | 609.631 | 61.3094 | 140.59 | 82.3463 | 108.619 | 104.682 | 126.703 | 145.901 | 47.0329 | 175.376 | 74.2063 | 223.84 | 54.4263 | 359.219 | 46.0555 | 475.768 | 15.5933 | 610.288 | 7.1053 | 671.78 | 11.3912
[6 empty] | 60.9427 | 180.161 | 81.9356 | 131.479 | 103.227 | 167.981 | 144.161 | 56.3086 | 173.457 | 87.0819 | 220.949 | 63.5514 | 353.517 | 54.2633 | 466.814 | 17.6872 | 595.816 | 8.0032 | 651.274 | 13.6241
[6 empty] | 60.6994 | 228.343 | 81.6085 | 152.91 | 102.507 | 204.967 | 142.299 | 67.6839 | 171.217 | 102.498 | 217.877 | 76.3134 | 348.602 | 63.2344 | 459.405 | 19.7834 | 579.364 | 9.2243 | 637.103 | 15.7974
[6 empty] | 60.4571 | 295.258 | 80.7965 | 188.077 | 101.996 | 254.895 | 140.742 | 80.3064 | 169.853 | 118.019 | 214.848 | 91.5467 | 344.788 | 72.9554 | 450.308 | 23.1234 | 564.495 | 10.6211 | 625.112 | 18.0807
[6 empty] | 60.276 | 365.348 | 80.5545 | 239.092 | 101.487 | 314.144 | 138.508 | 102.909 | 168.331 | 136.982 | 211.649 | 113.732 | 339.655 | 85.7854 | 443.604 | 26.3073 | 552.764 | 12.1319 | 606.637 | 22.128
[6 empty] | 60.2158 | 452.077 | 80.1527 | 309.777 | 101.082 | 384.849 | 136.719 | 130.562 | 166.989 | 161.233 | 208.916 | 135.89 | 335.268 | 98.7755 | 435.69 | 30.5342 | 541.819 | 13.7748 | 591.659 | 26.3073
[6 empty] | 60.0354 | 540.153 | 79.9926 | 416.069 | 100.477 | 487.287 | 134.819 | 168.823 | 165.328 | 191.684 | 206.63 | 161.717 | 331.269 | 113.846 | 430.924 | 34.2555 | 530.029 | 16.0522 | 577.051 | 31.2134
[6 empty] | 60.0954 | 598.755 | 80.0726 | 527.872 | 100.276 | 570.124 | 133.477 | 205.583 | 164.011 | 226.75 | 204.165 | 196.537 | 327.645 | 133.6 | 424.084 | 40.7659 | 522.138 | 17.9905 | 564.495 | 37.2573
[8 empty] | 80.0726 | 573.555 | 100.076 | 602.359 | 132.281 | 269.037 | 162.704 | 269.037 | 202.134 | 237.187 | 323.737 | 157.252 | 418.188 | 46.7516 | 512.823 | 20.6733 | 557.204 | 43.114
[8 empty] | 80.0726 | 598.157 |  |  | 131.358 | 324.359 | 161.892 | 311.329 | 200.523 | 280.858 | 320.836 | 180.883 | 412.374 | 55.4149 | 505.694 | 23.4025 | 545.625 | 53.0825
[12 empty] | 130.573 | 405.797 | 160.924 | 371.984 | 198.926 | 330.581 | 317.962 | 209.736 | 406.641 | 65.8809 | 497.17 | 27.5457 | 537.501 | 66.7429
[12 empty] | 130.051 | 501.625 | 159.961 | 451.625 | 197.341 | 414.408 | 314.798 | 245.145 | 401.791 | 77.0034 | 489.278 | 32.1639 | 530.029 | 79.3485
[12 empty] | 129.662 | 572.409 | 159.322 | 532.111 | 196.356 | 496.634 | 312.29 | 286.532 | 395.809 | 94.3347 | 481.512 | 38.7778 | 522.138 | 98.1846
[12 empty] | 129.662 | 602.359 | 158.686 | 573.555 | 196.16 | 566.713 | 310.422 | 325.985 | 391.87 | 109.273 | 474.818 | 45.8258 | 516.942 | 116.845
[14 empty] | 158.211 | 602.359 | 195.768 | 593.391 | 307.948 | 383.696 | 387.196 | 128.876 | 469.154 | 54.3176 | 511.799 | 140.449
[18 empty] | 305.8 | 445.792 | 383.727 | 148.985 | 461.707 | 67.5487 | 505.694 | 179.441
[18 empty] | 303.971 | 517.419 | 379.529 | 173.096 | 456.2 | 79.4278 | 501.664 | 217.859
[18 empty] | 302.152 | 570.694 | 375.753 | 209.108 | 450.308 | 95.4736 | 498.165 | 272.285
[18 empty] | 301.247 | 601.155 | 371.642 | 255.916 | 446.273 | 111.703 | 493.702 | 340.649
[20 empty] | 368.312 | 300.922 | 440.069 | 144.149 | 491.239 | 435.22
[20 empty] | 365.378 | 362.437 | 435.69 | 177.478 | 489.278 | 523.665
[20 empty] | 363.192 | 422.358 | 431.786 | 218.951 | 487.813 | 579.899
[20 empty] | 361.742 | 485.827 | 426.636 | 289.123 | 486.838 | 604.773
[20 empty] | 360.658 | 568.416 | 424.508 | 370.129
[20 empty] | 359.938 | 601.757 | 422.391 | 465.845
[22 empty] | 421.126 | 576.43
[22 empty] | 420.705 | 604.773